## Main
INPUT DATA
| Type of tent (1 = Frame, 2 = Hybrid, 3 = Pole) |  | 1 | [9 empty] | Assumptions:
| Length | (ft) | 40 | [9 empty] | Plate, if any, is attached to the upright at the footing with a pin connection. The connection is strong enough to resist of the weight of the plate and the ballast on top of the plate.
| Width | (ft) | 20 | [9 empty] | Method 2 (wind exposure) is important since it takes care of cases of method 1 that are strange (like negative ballast weights)
| Eave height | (ft) | 8 | [9 empty] | Method 2 includes valence
| Roof type (1 = G, 2 = H, 3 = P) |  | 3 |  | O = Open = Roof only (no walls) | [7 empty] | main35.6: IN PROGRESS - Include effect of valence by using the forces of the full walls (enclosed configuration) prorated by valence height.
| Ridge length if Hip roof | (ft) | 20 |  | E = Enclosed or Partially-enclosed = Roof and some walls with or without openings | [7 empty] | main36.0: Remove enclosed since a tent can never be fully enclosed
| Ridge length if any roof | (ft) | 0 | [9 empty] | main37.0: On recommence Gable
| Roof height | (ft) | 6 | [5 empty] | O | E |  |  | main38.0: Fixed valence, use 0.26 friction coeff for simple calculation of ballasts
| Roof pitch in width direction | (in/12in) | 7.2 |  |  |  | Total horizontal force in length | lbs | 94.3367 | 225.28 |  |  | main39.0: Fixed inconsistency issue with wind flow for open tents by changing the CN values for the load cases A and B for 3 levels of wind flow
| Roof pitch in length direction | (in/12in) | 3.6 |  |  |  | Total horizontal force in width | lbs | 163.84 | 460.9832 |  |  | main40.0: Switched the number of ballasts that resist Fx and Fy from all ballasts to only the windward ballast for pole tents and a combination of both for frame tents and hybrid tents.
| Wind speed | (mph) | 20 |  |  |  | Total vertical force | lbs | 698.1912 | 875.7032 |  |  | main40.1: Replaced "Wind Flow" with "Wind Exposure" and considered 3 levels of exposure.
| Wind exposure (1 = Fully exposd, 2 = Partially exposed, 3 = Sheltered) |  | 1 |  |  |  | Overturn moment about length | lbs.ft | 6857.1537 | 10432.1017
| Valence height | (ft) | 1 |  |  |  | Overturn moment about width | lbs.ft | 14953.243 | 17228.2922
SIMPLE CALCULATION OF BALLAST WEIGHTS
| Assume 1 ballast per intermediate post | [7 empty] | O | E
| Assume Fixed-to-pole configuration | [5 empty] | Individual ballast weight | lbs | 213.3047 | 464.0654
| Number of intermediate posts in length |  | 1 |  |  |  |  | Friction coeff | 0.26 | 0.26
| Number of intermediate posts in width |  | 1 |  |  |  |  | Ballast weight to resist Fx | 159.8406 | 282.7552
| Number of ballasts per corner post |  | 1 |  |  |  |  | Ballast weight to resist Fy | 213.3047 | 464.0654
| Total number of ballasts |  | 8 |  |  |  |  | Ballast weight to resist Fz | 87.2739 | 109.4629
| lambda (for Nc) |  | 0.71 |  |  |  |  | Ballast weight to resist Mx | 85.7144 | 130.4013
[8 empty] | Ballast weight to resist My | 93.4578 | 107.6768
ADVANCED CALCULATION OF BALLAST WEIGHTS
Type of ballast (ie, concrete, steel, plastic) is not as important as dimensions
Type of ground surface (smooth/rough, dry/wet, concrete, asphalt, gravel, grass) is not as important as dimensions
Type of modifier (plywood, rubber, neoprene) is not as important as dimensions
For a given set of dimensions, give the weights for highest and lowest friction coefficients to provide range
B
|  |  |  | Fixed-to-Plate |  | Fixed-to-Pole |  | A |  | B assuming A |  | B assuming C |  | C |  | D
|  | Distance between center of ballast and upright (ft) | d1 |  |  |  |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  | Distance between far end of plate and upright (ft) | d2 |  |  |  |  | 5 | 5 | 5 | 5 |  |  |  |  | 5 | 5
|  | Ballast effective width (ft) | d3 | [8 empty] | 1.2 | 1.2 | 1.2 | 1.2
|  | Horizontal distance between guy attachment point and pole (ft) | d4 | [8 empty] | 0 | 0 | 3 | 3 | 2 | 2 |  | G | 5.831
|  | Vertical distance between plate and guy attachment point (ft) | h4 | [8 empty] | 3 | 3 | 3 | 3 |  |  |  | cos(alpha) | 0.5145
|  | Horizontal distance between guy attachment point and upright (ft) | d5 | [12 empty] | 2 | 2 |  | sin(alpha) | 0.85749
|  | Friction coefficient between ballast and ground (if applicable) | mu1 |  |  | 0.5 | 0.5 | [6 empty] | 0.5 | 0.5 |  |  |  | tan(alpha) | 1.6667
|  | Friction coefficient between ballast and plate (if any) | mu2 | [8 empty] | 0.5 | 0.5 | [5 empty] | 1 | 1
|  | Friction coefficient between plate and ground (if any) | mu3 | 0.5 | 0.5 |  |  | 0.5 | 0.5 | 0.5 | 0.5 |  |  |  |  | 0.5 | 0.5 |  | B | 3.43
|  | Weight of plate (if any) | Wplate | 50 | 50 |  |  | 50 | 50 | 50 | 50 | 50 | 50 |  |  | 50 | 50 |  | Fh | 38.9821
|  | Angle of guy | tan(alpha) | [8 empty] | 1.6667 | 1.6667 | 1.6667 | 1.6667 | 4 | 4 |  | Fv | 87.2739
|  |  | Fh in x | [6 empty] | 11.7921 | 28.16 |  |  |  |  | 38.9821 | 93.0909 |  | Cond. 1 | 259.8808
|  |  | Fh in y | [6 empty] | 20.48 | 57.6229 |  |  |  |  | 67.7025 | 190.4889 |  | Cond. 2 | 349.0956
|  |  |  | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed |  | Cond. 3 | 142.9345
|  |  | Ballast weight to resist Fx | 125.0086 | 199.5749 | 125.0086 | 199.5749 | 205.6848 | 261.1573 | 205.6848 | 261.1573 | 259.8808 | 620.6061 | 259.8808 | 620.6061 | 218.2142 | 578.9394 |  | Cond. 4 | 192.0026
|  |  | Ballast weight to resist Fy | 152.8099 | 293.8562 | 152.8099 | 293.8562 | 205.6848 | 263.124 | 205.6848 | 263.124 | 451.3499 | 1269.9262 | 451.3499 | 1269.9262 | 409.6832 | 1228.2595
|  |  | Ballast weight to resist Fz | 87.2739 | 109.4629 | 87.2739 | 109.4629 | 205.6848 | 261.1573 | 205.6848 | 261.1573 | 87.2739 | 109.4629 | 87.2739 | 109.4629 | 103.7898 | 140.7715
|  |  | Ballast weight to resist Mx | 85.7144 | 130.4013 | 85.7144 | 130.4013 | 201.7861 | 313.5032 | 201.7861 | 313.5032 | 342.8577 | 521.6051 | 342.8577 | 521.6051 | 101.1907 | 175.6688
|  |  | Ballast weight to resist My | 93.4578 | 107.6768 | 93.4578 | 107.6768 | 221.1444 | 256.6921 | 221.1444 | 256.6921 | 373.8311 | 430.7073 | 373.8311 | 430.7073 | 114.0963 | 137.7947
|  |  |  | Fixed-to-plate |  | Fixed-to-pole |  | A |  | B |  |  |  | C |  | D
|  |  |  | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed | Open | Enclosed
|  |  | Intermediate | [6 empty] | 221.1444 | 313.5032 | 451.3499 | 1269.9262
|  |  | Recommended weight (including weight of plate if any) | 152.8099 | 293.8562 | 152.8099 | 293.8562 | 221.1444 | 313.5032 | 451.3499 | 1269.9262 |  |  | 451.3499 | 1269.9262 | 409.6832 | 1228.2595
|  |  | Recommended weight to resist sliding (including weight of plate if any) | 152.8099 | 293.8562 | 152.8099 | 293.8562 | 205.6848 | 263.124 | 451.3499 | 1269.9262 |  |  | 451.3499 | 1269.9262 | 409.6832 | 1228.2595
|  |  | Recommended weight to resist lift and overturn (including weight of plate if any) | 93.4578 | 130.4013 | 93.4578 | 130.4013 | 221.1444 | 313.5032 | 373.8311 | 521.6051 |  |  | 373.8311 | 521.6051 | 114.0963 | 175.6688
[7 empty] | Ground surface (1 = Smooth concrete, 2 = Rough concrete, 3 = Asphalt, 4 = Gravel, 5 = Dirt, 6 = Grass) | 1 |  | 205.6848 | 263.124 | 451.3499 | 1269.9262
[7 empty] | Ballast type (1 = Plastic barrel, 2 = Steel drum, 3 = Concrete block) | 1 |  | 221.1444 | 313.5032 | 373.8311 | 521.6051
[7 empty] | Ground modifier (1 = Rubber pad, 2 = Neoprene pad, 3 = Plywood, 4 = Metal sheet) | 1
[7 empty] | Ballast modifier (1 = Rubber pad, 2 = Neoprene pad, 3 = Plywood, 4 = Metal sheet) | 1
OUTPUT
[10 empty] | OPEN | PART-ENC |  |  | Method used to calculate loads
[8 empty] | Total horizontal force in length | lbs | -94.3367 | -225.28 |  |  | 1 | 2
[8 empty] | Total horizontal force in width | lbs | -163.84 | -460.9832 |  |  | 2 | 1
[8 empty] | Total vertical force | lbs | 698.1912 | 875.7032 |  |  | 1 | 1
[8 empty] | Overturn moment about length | lbs.ft | 6857.1537 | 10432.1017 |  |  | 1 | 1
[8 empty] | Overturn moment about width | lbs.ft | 14953.243 | 17228.2922 |  |  | 1 | 1
[8 empty] | Weight of each balast | lbs | 93.4578 | 221.6265
| INPUT DATA |  |  |  | OUTPUT |  |  |  |  | Method 1: Code |  |  |  | Method 2: Wind exposure
| Length | (ft) | 40 | [6 empty] | OPEN | PART-ENC |  |  | OPEN | PART-ENC |  |  | Method 3: Sail lift |  |  |  | Method 4: Wind exposure with initiated overturn
| Width | (ft) | 20 |  |  |  |  | Total horizontal force in length | lbs | -94.3367 | -189.2031 |  |  | -81.92 | -225.28
| Eave height | (ft) | 8 |  |  |  |  | Total horizontal force in width | lbs | -150.0861 | -460.9832 |  |  | -163.84 | -450.56
| Roof type (1 = G, 2 = H, 3 = P) |  | 3 |  |  |  |  | Total vertical force | lbs | 698.1912 | 875.7032
| Ridge length if Hip roof | (ft) | 20 |  |  |  |  | Overturn moment about length | lbs.ft | 6857.1537 | 10432.1017 |  |  | 1536 | 2539.52
| Ridge length if any roof | (ft) | 0 |  |  |  |  | Overturn moment about width | lbs.ft | 14953.243 | 17228.2922 |  |  | 768 | 1269.76
| Roof height | (ft) | 6 |  |  | ATTENTION, Fz DOES NOT HAVE A CUMMULATIVE EFFECT WITH OVERTURN MOMENTS SINCE OVERTURN MOMENTS ARE CALCULATED FROM FORCES
| Roof pitch in width direction | (in/12in) | 7.2 |  |  | ATTENTION, FOR CONF. A AND B, THE BALLASTS OF THE SIDES PARALLEL TO THE WIND ARE ASSUMED TO RESISTS SLIDING THE SAME AMOUNT AS THE WINDWARD AND LEEWARD BALLASTS.
| Roof pitch in length direction | (in/12in) | 3.6 |  |  | ATTENTION, INTERPOLATION BETWEEN POSITIVE AND NEGATIVE TERMS IS NOT ALLOWED!
| Wind speed | (mph) | 20 |  |  | ATTENTION, CONSIDER THE WORST CASE SCENARIO FOR CLEAR AND OBSTRUCTED WIND FLOW BECAUSE IT IS NOT CLEAR!!
|  | Wind flow (1 = clear, 2, 3 = obstructed) | 1 |  |  | ATTENTION, ADD A CONDITION IN THE ONLINE FORM TO USE THE DATA OF GABLE ROOF WHEN HIP IS SELECTED WITH RIDGE LENGTH EQUAL TO LENGTH. THE RESULTS ARE DIFFERENT B/C VERTICAL PART OF THE ROOF IS CONSIDERED DIFFERENTLY WHEN HIP (FAKE GABLE) AND GABLE.
| Valance height | (ft) | 1 |  |  | ATTENTION, IN ALL CONFIGURATIONS, WHEN CONSIDERING SLIDING DUE TO FX OR FY (WITH FZ), THE LOCAL FORCES APPLIED AT THE TOP OF UPRIGHT (Fh AND Fv) ASSUME THAT Fh RESISTS ALL FX OR FY AND THE FOOTING DOES NOT RESIST ANYTHING. IS THIS A GOOD ASSUMPTION?
ATTENTION, WHAT IF WIND IS IN DIAGONAL DIRECTION?
CALCULATION OF BALLAST WEIGHTS
Assume 1 ballast per intermediate post
| Number of intermediate posts in length |  | 1
| Number of intermediate posts in width |  | 1
| Number of ballasts per corner post |  | 1 | [5 empty] | -
| Friction coefficient |  | 0.26
| Total number of ballasts |  | 8
Unacceptable slight move of ballasts (use only windward ballasts)
[10 empty] | OPEN | PART-ENC |  |  | Critical load used to calculate ballasts
[8 empty] | Ballast weight based on drag in length and friction (use only windward ballasts) | lbs | 120.9445 | 288.8205
[8 empty] | Ballast weight based on drag in width and friction (use only windward ballasts) | lbs | 210.0513 | 591.0041 |  |  | Fy | Fy
[8 empty] | Individual ballast weight based on vertical force | lbs | 87.2739 | 109.4629
[8 empty] | Individual ballast weight based on overturn about length | lbs | 85.7144 | 130.4013
[8 empty] | Individual ballast weight based on overturn about width | lbs | 93.4578 | 107.6768
[8 empty] | Weight of each ballast | lbs | 210.0513 | 591.0041
Fixed configuration (use all ballasts)
[10 empty] | OPEN | PART-ENC
[8 empty] | Ballast weight based on drag in length and friction (use all ballasts) | lbs | 45.3542 | 108.3077
[8 empty] | Ballast weight based on drag in width and friction (use all ballasts) | lbs | 78.7692 | 221.6265 |  |  |  | Fy
[8 empty] | Individual ballast weight based on vertical force | lbs | 87.2739 | 109.4629
[8 empty] | Individual ballast weight based on overturn about length | lbs | 85.7144 | 130.4013
[8 empty] | Individual ballast weight based on overturn about width | lbs | 93.4578 | 107.6768 |  |  | My
[8 empty] | Weight of each ballast | lbs | 93.4578 | 221.6265
Tent definition | [12 empty] | ALL RESULTS |  |  |  | Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition
1 | X-dimension | (ft) | 40 | [5 empty] | OPEN | PART-ENC |  |  | OPEN | Part-Encl |  |  | 2 | X-dimension | (ft) | 40 | [5 empty] | OPEN | PART-ENC | [6 empty] | 3 | X-dimension | (ft) | 40 | [5 empty] | OPEN | PART-ENC | [6 empty] | 4 | X-dimension | (ft) | 40 | [5 empty] | OPEN | PART-ENC | [6 empty] | 5 | X-dimension | (ft) | 40 | [5 empty] | OPEN | PART-ENC | [6 empty] | 6 | X-dimension | (ft) | 40 | [5 empty] | OPEN | PART-ENC | [6 empty] | 7 | X-dimension | (ft) | 40 | [5 empty] | OPEN | PART-ENC | [6 empty] | 8 | X-dimension | (ft) | 40 | [5 empty] | OPEN | PART-ENC
1 | Y-dimension | (ft) | 20 |  |  |  | Total horizontal force (+ in X) | lbs | -94.3367 | -162.4136 |  |  | -94.3367 | -189.2031 |  |  | 2 | Y-dimension | (ft) | 20 |  |  |  | Total horizontal force (+ in X) | lbs | -78.1959 | -189.2031 | [6 empty] | 3 | Y-dimension | (ft) | 20 |  |  |  | Total horizontal force (+ in X) | lbs | -11.4051 | -162.4136 | [6 empty] | 4 | Y-dimension | (ft) | 20 |  |  |  | Total horizontal force (+ in X) | lbs | -72.3114 | -189.2031 | [6 empty] | 5 | Y-dimension | (ft) | 20 |  |  |  | Total horizontal force (+ in X) | lbs | 3.5527e-15 | 3.5527e-15 | [6 empty] | 6 | Y-dimension | (ft) | 20 |  |  |  | Total horizontal force (+ in X) | lbs | -3.5527e-15 | 0 | [6 empty] | 7 | Y-dimension | (ft) | 20 |  |  |  | Total horizontal force (+ in X) | lbs | 3.5527e-15 | 0 | [6 empty] | 8 | Y-dimension | (ft) | 20 |  |  |  | Total horizontal force (+ in X) | lbs | 1.7764e-15 | 0
1 | Eave height | (ft) | 8 |  |  |  | Total horizontal force (+ in Y) | lbs | 0 | 0 |  |  | -150.0861 | -460.9832 |  |  | 2 | Eave height | (ft) | 8 |  |  |  | Total horizontal force (+ in Y) | lbs | 0 | 0 | [6 empty] | 3 | Eave height | (ft) | 8 |  |  |  | Total horizontal force (+ in Y) | lbs | 0 | 0 | [6 empty] | 4 | Eave height | (ft) | 8 |  |  |  | Total horizontal force (+ in Y) | lbs | 0 | 0 | [6 empty] | 5 | Eave height | (ft) | 8 |  |  |  | Total horizontal force (+ in Y) | lbs | -150.0861 | -415.2056 | [6 empty] | 6 | Eave height | (ft) | 8 |  |  |  | Total horizontal force (+ in Y) | lbs | -127.1822 | -460.9832 | [6 empty] | 7 | Eave height | (ft) | 8 |  |  |  | Total horizontal force (+ in Y) | lbs | -46.629 | -415.2056 | [6 empty] | 8 | Eave height | (ft) | 8 |  |  |  | Total horizontal force (+ in Y) | lbs | -139.3256 | -460.9832
1 | Band height | (ft) | 1 |  |  |  | Total vertical force (+ in Z) | lbs | 36.6246 | 812.3943 |  |  | 698.1912 | 875.7032 |  |  | 2 | Band height | (ft) | 1 |  |  |  | Total vertical force (+ in Z) | lbs | 8.7148 | 615.6697 | [6 empty] | 3 | Band height | (ft) | 1 |  |  |  | Total vertical force (+ in Z) | lbs | 698.1912 | -115.9662 | [6 empty] | 4 | Band height | (ft) | 1 |  |  |  | Total vertical force (+ in Z) | lbs | 256.4543 | -312.6907 | [6 empty] | 5 | Band height | (ft) | 1 |  |  |  | Total vertical force (+ in Z) | lbs | -35.9673 | 875.7032 | [6 empty] | 6 | Band height | (ft) | 1 |  |  |  | Total vertical force (+ in Z) | lbs | -68.6345 | 597.3692 | [6 empty] | 7 | Band height | (ft) | 1 |  |  |  | Total vertical force (+ in Z) | lbs | 633.3115 | -52.6572 | [6 empty] | 8 | Band height | (ft) | 1 |  |  |  | Total vertical force (+ in Z) | lbs | 51.4981 | -330.9913
1 | Roof pitch in Y | in/12in | 7.2 |  |  |  | Overturn moment | lbs.ft | -1203.3414 | 17228.2922 |  |  | 6857.1537 | 10432.1017 |  |  | 2 | Roof pitch in Y | in/12in | 7.2 |  |  |  | Overturn moment | lbs.ft | -2130.2349 | 11863.7508 | [6 empty] | 3 | Roof pitch in Y | in/12in | 7.2 |  |  |  | Overturn moment | lbs.ft | 14953.243 | -1338.9171 | [6 empty] | 4 | Roof pitch in Y | in/12in | 7.2 |  |  |  | Overturn moment | lbs.ft | 3233.3981 | -6703.4585 | [6 empty] | 5 | Roof pitch in Y | in/12in | 7.2 |  |  |  | Overturn moment | lbs.ft | -8.6943 | 10432.1017 | [6 empty] | 6 | Roof pitch in Y | in/12in | 7.2 |  |  |  | Overturn moment | lbs.ft | -600.4515 | 7368.0968 | [6 empty] | 7 | Roof pitch in Y | in/12in | 7.2 |  |  |  | Overturn moment | lbs.ft | 6857.1537 | 1148.4971 | [6 empty] | 8 | Roof pitch in Y | in/12in | 7.2 |  |  |  | Overturn moment | lbs.ft | 761.7023 | -1915.5078
1 | Roof pitch in X | in/12in | 3.6 | [5 empty] | Must ALWAYS be POSITIVE for overturn |  |  |  | 14953.243 | 17228.2922 |  |  | 2 | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) |  |  |  |  | Must ALWAYS be POSITIVE for overturn | [7 empty] | 3 | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) |  |  |  |  | Must ALWAYS be POSITIVE for overturn | [7 empty] | 4 | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) |  |  |  |  | Must ALWAYS be POSITIVE for overturn | [7 empty] | 5 | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) |  |  |  |  | Must ALWAYS be POSITIVE for overturn | [7 empty] | 6 | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) |  |  |  |  | Must ALWAYS be POSITIVE for overturn | [7 empty] | 7 | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) |  |  |  |  | Must ALWAYS be POSITIVE for overturn | [7 empty] | 8 | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) |  |  |  |  | Must ALWAYS be POSITIVE for overturn
1 |  |  | Case 1 | [13 empty] | 2 |  |  | Case 1 | [13 empty] | 3 |  |  | Case 1 | [13 empty] | 4 |  |  | Case 1 | [13 empty] | 5 |  |  | Case 1 | [13 empty] | 6 |  |  | Case 1 | [13 empty] | 7 |  |  | Case 1 | [13 empty] | 8 |  |  | Case 1
1 |  | Wind direction (X or Y) | X | [13 empty] | 2 |  | Wind direction (X or Y) | X | [13 empty] | 3 |  | Wind direction (X or Y) | X | [13 empty] | 4 |  | Wind direction (X or Y) | X | [13 empty] | 5 |  | Wind direction (X or Y) | Y | [13 empty] | 6 |  | Wind direction (X or Y) | Y | [13 empty] | 7 |  | Wind direction (X or Y) | Y | [13 empty] | 8 |  | Wind direction (X or Y) | Y
1 |  | Wind speed (mph) from Step 2 | 20 | [13 empty] | 2 |  | Wind speed (mph) from Step 2 | 20 | [13 empty] | 3 |  | Wind speed (mph) from Step 2 | 20 | [13 empty] | 4 |  | Wind speed (mph) from Step 2 | 20 | [13 empty] | 5 |  | Wind speed (mph) from Step 2 | 20 | [13 empty] | 6 |  | Wind speed (mph) from Step 2 | 20 | [13 empty] | 7 |  | Wind speed (mph) from Step 2 | 20 | [13 empty] | 8 |  | Wind speed (mph) from Step 2 | 20
1 |  | Case 1 or 2 for Internal pressure coefficient (GCpi) in Step 3 | 1 | [13 empty] | 2 |  | Case 1 or 2 for Internal pressure coefficient (GCpi) in Step 3 | 1 | [13 empty] | 3 |  | Case 1 or 2 for Internal pressure coefficient (GCpi) in Step 3 | 2 | [13 empty] | 4 |  | Case 1 or 2 for Internal pressure coefficient (GCpi) in Step 3 | 2 | [13 empty] | 5 |  | Case 1 or 2 for Internal pressure coefficient (GCpi) in Step 3 | 1 | [13 empty] | 6 |  | Case 1 or 2 for Internal pressure coefficient (GCpi) in Step 3 | 1 | [13 empty] | 7 |  | Case 1 or 2 for Internal pressure coefficient (GCpi) in Step 3 | 2 | [13 empty] | 8 |  | Case 1 or 2 for Internal pressure coefficient (GCpi) in Step 3 | 2
1 |  | Load case (A or B, both must be tested) for CN or Cp in Step 6 | A | [13 empty] | 2 |  | Load case (A or B, both must be tested) for CN or Cp in Step 6 | B | [13 empty] | 3 |  | Load case (A or B, both must be tested) for CN or Cp in Step 6 | A | [13 empty] | 4 |  | Load case (A or B, both must be tested) for CN or Cp in Step 6 | B | [13 empty] | 5 |  | Load case (A or B, both must be tested) for CN or Cp in Step 6 | A | [13 empty] | 6 |  | Load case (A or B, both must be tested) for CN or Cp in Step 6 | B | [13 empty] | 7 |  | Load case (A or B, both must be tested) for CN or Cp in Step 6 | A | [13 empty] | 8 |  | Load case (A or B, both must be tested) for CN or Cp in Step 6 | B
1 |  | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [12 empty] | 2 |  | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [12 empty] | 3 |  | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [12 empty] | 4 |  | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [12 empty] | 5 |  | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [12 empty] | 6 |  | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [12 empty] | 7 |  | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [12 empty] | 8 |  | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3)
1 |  |  | D | This is used at 2 locations: exposure category for Kz (Step 4) and CN (Step 6) | [12 empty] | 2 |  |  | D | This is used at 2 locations: exposure category for Kz (Step 4) and CN (Step 6) | [12 empty] | 3 |  |  | D | This is used at 2 locations: exposure category for Kz (Step 4) and CN (Step 6) | [12 empty] | 4 |  |  | D | This is used at 2 locations: exposure category for Kz (Step 4) and CN (Step 6) | [12 empty] | 5 |  |  | D | This is used at 2 locations: exposure category for Kz (Step 4) and CN (Step 6) | [12 empty] | 6 |  |  | D | This is used at 2 locations: exposure category for Kz (Step 4) and CN (Step 6) | [12 empty] | 7 |  |  | D | This is used at 2 locations: exposure category for Kz (Step 4) and CN (Step 6) | [12 empty] | 8 |  |  | D | This is used at 2 locations: exposure category for Kz (Step 4) and CN (Step 6)
1 |  |  |  | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [12 empty] | 2 |  |  |  | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [12 empty] | 3 |  |  |  | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [12 empty] | 4 |  |  |  | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [12 empty] | 5 |  |  |  | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [12 empty] | 6 |  |  |  | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [12 empty] | 7 |  |  |  | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [12 empty] | 8 |  |  |  | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach)
1 |  |  |  | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [12 empty] | 2 |  |  |  | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [12 empty] | 3 |  |  |  | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [12 empty] | 4 |  |  |  | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [12 empty] | 5 |  |  |  | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [12 empty] | 6 |  |  |  | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [12 empty] | 7 |  |  |  | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [12 empty] | 8 |  |  |  | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%.
1 |  |  |  | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [12 empty] | 2 |  |  |  | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [12 empty] | 3 |  |  |  | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [12 empty] | 4 |  |  |  | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [12 empty] | 5 |  |  |  | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [12 empty] | 6 |  |  |  | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [12 empty] | 7 |  |  |  | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [12 empty] | 8 |  |  |  | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff)
1 |  |  |  | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [12 empty] | 2 |  |  |  | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [12 empty] | 3 |  |  |  | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [12 empty] | 4 |  |  |  | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [12 empty] | 5 |  |  |  | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [12 empty] | 6 |  |  |  | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [12 empty] | 7 |  |  |  | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [12 empty] | 8 |  |  |  | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively
1 | Ridge length in X | (ft) | 0 | [13 empty] | 2 | Ridge length in X | (ft) | 0 | [13 empty] | 3 | Ridge length in X | (ft) | 0 | [13 empty] | 4 | Ridge length in X | (ft) | 0 | [13 empty] | 5 | Ridge length in X | (ft) | 0 | [13 empty] | 6 | Ridge length in X | (ft) | 0 | [13 empty] | 7 | Ridge length in X | (ft) | 0 | [13 empty] | 8 | Ridge length in X | (ft) | 0
1 | Ridge length in Y | (ft) | 0 | [13 empty] | 2 | Ridge length in Y | (ft) | 0 | [13 empty] | 3 | Ridge length in Y | (ft) | 0 | [13 empty] | 4 | Ridge length in Y | (ft) | 0 | [13 empty] | 5 | Ridge length in Y | (ft) | 0 | [13 empty] | 6 | Ridge length in Y | (ft) | 0 | [13 empty] | 7 | Ridge length in Y | (ft) | 0 | [13 empty] | 8 | Ridge length in Y | (ft) | 0
1 | Pitch angle in Y | (deg) | 30.9638 | [13 empty] | 2 | Pitch angle in Y | (deg) | 30.9638 | [13 empty] | 3 | Pitch angle in Y | (deg) | 30.9638 | [13 empty] | 4 | Pitch angle in Y | (deg) | 30.9638 | [13 empty] | 5 | Pitch angle in Y | (deg) | 30.9638 | [13 empty] | 6 | Pitch angle in Y | (deg) | 30.9638 | [13 empty] | 7 | Pitch angle in Y | (deg) | 30.9638 | [13 empty] | 8 | Pitch angle in Y | (deg) | 30.9638
1 | Pitch angle in X | (deg) | 16.6993 | [13 empty] | 2 | Pitch angle in X | (deg) | 16.6993 | [13 empty] | 3 | Pitch angle in X | (deg) | 16.6993 | [13 empty] | 4 | Pitch angle in X | (deg) | 16.6993 | [13 empty] | 5 | Pitch angle in X | (deg) | 16.6993 | [13 empty] | 6 | Pitch angle in X | (deg) | 16.6993 | [13 empty] | 7 | Pitch angle in X | (deg) | 16.6993 | [13 empty] | 8 | Pitch angle in X | (deg) | 16.6993
1 | Check pitch in Y is > 10 deg |  | OK | [13 empty] | 2 | Check pitch in Y is > 10 deg |  | OK | [13 empty] | 3 | Check pitch in Y is > 10 deg |  | OK | [13 empty] | 4 | Check pitch in Y is > 10 deg |  | OK | [13 empty] | 5 | Check pitch in Y is > 10 deg |  | OK | [13 empty] | 6 | Check pitch in Y is > 10 deg |  | OK | [13 empty] | 7 | Check pitch in Y is > 10 deg |  | OK | [13 empty] | 8 | Check pitch in Y is > 10 deg |  | OK
1 | Check pitch in X is > 10 deg |  | OK | [13 empty] | 2 | Check pitch in X is > 10 deg |  | OK | [13 empty] | 3 | Check pitch in X is > 10 deg |  | OK | [13 empty] | 4 | Check pitch in X is > 10 deg |  | OK | [13 empty] | 5 | Check pitch in X is > 10 deg |  | OK | [13 empty] | 6 | Check pitch in X is > 10 deg |  | OK | [13 empty] | 7 | Check pitch in X is > 10 deg |  | OK | [13 empty] | 8 | Check pitch in X is > 10 deg |  | OK
1 | Roof height | (ft) | 6 | [13 empty] | 2 | Roof height | (ft) | 6 | [13 empty] | 3 | Roof height | (ft) | 6 | [13 empty] | 4 | Roof height | (ft) | 6 | [13 empty] | 5 | Roof height | (ft) | 6 | [13 empty] | 6 | Roof height | (ft) | 6 | [13 empty] | 7 | Roof height | (ft) | 6 | [13 empty] | 8 | Roof height | (ft) | 6
1 | Mean roof height | (ft) | 11 | [13 empty] | 2 | Mean roof height | (ft) | 11 | [13 empty] | 3 | Mean roof height | (ft) | 11 | [13 empty] | 4 | Mean roof height | (ft) | 11 | [13 empty] | 5 | Mean roof height | (ft) | 11 | [13 empty] | 6 | Mean roof height | (ft) | 11 | [13 empty] | 7 | Mean roof height | (ft) | 11 | [13 empty] | 8 | Mean roof height | (ft) | 11
1 | [16 empty] | 2 | [16 empty] | 3 | [16 empty] | 4 | [16 empty] | 5 | [16 empty] | 6 | [16 empty] | 7 | [16 empty] | 8
1 |  | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [12 empty] | 2 |  | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [12 empty] | 3 |  | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [12 empty] | 4 |  | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [12 empty] | 5 |  | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [12 empty] | 6 |  | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [12 empty] | 7 |  | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [12 empty] | 8 |  | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail.
1 |  |  |  | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [12 empty] | 2 |  |  |  | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [12 empty] | 3 |  |  |  | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [12 empty] | 4 |  |  |  | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [12 empty] | 5 |  |  |  | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [12 empty] | 6 |  |  |  | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [12 empty] | 7 |  |  |  | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [12 empty] | 8 |  |  |  | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings.
1 |  |  |  | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [12 empty] | 2 |  |  |  | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [12 empty] | 3 |  |  |  | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [12 empty] | 4 |  |  |  | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [12 empty] | 5 |  |  |  | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [12 empty] | 6 |  |  |  | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [12 empty] | 7 |  |  |  | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [12 empty] | 8 |  |  |  | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls.
1 |  |  |  | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [12 empty] | 2 |  |  |  | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [12 empty] | 3 |  |  |  | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [12 empty] | 4 |  |  |  | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [12 empty] | 5 |  |  |  | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [12 empty] | 6 |  |  |  | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [12 empty] | 7 |  |  |  | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [12 empty] | 8 |  |  |  | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation.
1 | [16 empty] | 2 | [16 empty] | 3 | [16 empty] | 4 | [16 empty] | 5 | [16 empty] | 6 | [16 empty] | 7 | [16 empty] | 8
TENT | [16 empty] | TENT | [16 empty] | TENT | [16 empty] | TENT | [16 empty] | TENT | [16 empty] | TENT | [16 empty] | TENT | [16 empty] | TENT
Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition | [16 empty] | Tent definition
| X-dimension | (ft) | 40 | [14 empty] | X-dimension | (ft) | 40 | [14 empty] | X-dimension | (ft) | 40 | [14 empty] | X-dimension | (ft) | 40 | [14 empty] | X-dimension | (ft) | 40 | [14 empty] | X-dimension | (ft) | 40 | [14 empty] | X-dimension | (ft) | 40 | [14 empty] | X-dimension | (ft) | 40
| Y-dimension | (ft) | 20 | [14 empty] | Y-dimension | (ft) | 20 | [14 empty] | Y-dimension | (ft) | 20 | [14 empty] | Y-dimension | (ft) | 20 | [14 empty] | Y-dimension | (ft) | 20 | [14 empty] | Y-dimension | (ft) | 20 | [14 empty] | Y-dimension | (ft) | 20 | [14 empty] | Y-dimension | (ft) | 20
| Eave height | (ft) | 8 | [14 empty] | Eave height | (ft) | 8 | [14 empty] | Eave height | (ft) | 8 | [14 empty] | Eave height | (ft) | 8 | [14 empty] | Eave height | (ft) | 8 | [14 empty] | Eave height | (ft) | 8 | [14 empty] | Eave height | (ft) | 8 | [14 empty] | Eave height | (ft) | 8
| Band height | (ft) | 1 | [14 empty] | Band height | (ft) | 1 | [14 empty] | Band height | (ft) | 1 | [14 empty] | Band height | (ft) | 1 | [14 empty] | Band height | (ft) | 1 | [14 empty] | Band height | (ft) | 1 | [14 empty] | Band height | (ft) | 1 | [14 empty] | Band height | (ft) | 1
| Roof pitch in Y | in/12in | 7.2 | [14 empty] | Roof pitch in Y | in/12in | 7.2 | [14 empty] | Roof pitch in Y | in/12in | 7.2 | [14 empty] | Roof pitch in Y | in/12in | 7.2 | [14 empty] | Roof pitch in Y | in/12in | 7.2 | [14 empty] | Roof pitch in Y | in/12in | 7.2 | [14 empty] | Roof pitch in Y | in/12in | 7.2 | [14 empty] | Roof pitch in Y | in/12in | 7.2
| Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) | [13 empty] | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) | [13 empty] | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) | [13 empty] | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) | [13 empty] | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) | [13 empty] | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) | [13 empty] | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical) | [13 empty] | Roof pitch in X | in/12in | 3.6 | (Enter 0 if vertical)
| Ridge length in X | (ft) | 0 | [14 empty] | Ridge length in X | (ft) | 0 | [14 empty] | Ridge length in X | (ft) | 0 | [14 empty] | Ridge length in X | (ft) | 0 | [14 empty] | Ridge length in X | (ft) | 0 | [14 empty] | Ridge length in X | (ft) | 0 | [14 empty] | Ridge length in X | (ft) | 0 | [14 empty] | Ridge length in X | (ft) | 0
| Ridge length in Y | (ft) | 0 | [14 empty] | Ridge length in Y | (ft) | 0 | [14 empty] | Ridge length in Y | (ft) | 0 | [14 empty] | Ridge length in Y | (ft) | 0 | [14 empty] | Ridge length in Y | (ft) | 0 | [14 empty] | Ridge length in Y | (ft) | 0 | [14 empty] | Ridge length in Y | (ft) | 0 | [14 empty] | Ridge length in Y | (ft) | 0
| Pitch angle in Y | (deg) | 30.9638 | [14 empty] | Pitch angle in Y | (deg) | 30.9638 | [14 empty] | Pitch angle in Y | (deg) | 30.9638 | [14 empty] | Pitch angle in Y | (deg) | 30.9638 | [14 empty] | Pitch angle in Y | (deg) | 30.9638 | [14 empty] | Pitch angle in Y | (deg) | 30.9638 | [14 empty] | Pitch angle in Y | (deg) | 30.9638 | [14 empty] | Pitch angle in Y | (deg) | 30.9638
| Pitch angle in X | (deg) | 16.6993 | [14 empty] | Pitch angle in X | (deg) | 16.6993 | [14 empty] | Pitch angle in X | (deg) | 16.6993 | [14 empty] | Pitch angle in X | (deg) | 16.6993 | [14 empty] | Pitch angle in X | (deg) | 16.6993 | [14 empty] | Pitch angle in X | (deg) | 16.6993 | [14 empty] | Pitch angle in X | (deg) | 16.6993 | [14 empty] | Pitch angle in X | (deg) | 16.6993
| Check pitch in Y is > 10 deg |  | OK | [14 empty] | Check pitch in Y is > 10 deg |  | OK | [14 empty] | Check pitch in Y is > 10 deg |  | OK | [14 empty] | Check pitch in Y is > 10 deg |  | OK | [14 empty] | Check pitch in Y is > 10 deg |  | OK | [14 empty] | Check pitch in Y is > 10 deg |  | OK | [14 empty] | Check pitch in Y is > 10 deg |  | OK | [14 empty] | Check pitch in Y is > 10 deg |  | OK
| Check pitch in X is > 10 deg |  | OK | [14 empty] | Check pitch in X is > 10 deg |  | OK | [14 empty] | Check pitch in X is > 10 deg |  | OK | [14 empty] | Check pitch in X is > 10 deg |  | OK | [14 empty] | Check pitch in X is > 10 deg |  | OK | [14 empty] | Check pitch in X is > 10 deg |  | OK | [14 empty] | Check pitch in X is > 10 deg |  | OK | [14 empty] | Check pitch in X is > 10 deg |  | OK
| Roof height | (ft) | 6 | [14 empty] | Roof height | (ft) | 6 | [14 empty] | Roof height | (ft) | 6 | [14 empty] | Roof height | (ft) | 6 | [14 empty] | Roof height | (ft) | 6 | [14 empty] | Roof height | (ft) | 6 | [14 empty] | Roof height | (ft) | 6 | [14 empty] | Roof height | (ft) | 6
| Mean roof height | (ft) | 11 | [14 empty] | Mean roof height | (ft) | 11 | [14 empty] | Mean roof height | (ft) | 11 | [14 empty] | Mean roof height | (ft) | 11 | [14 empty] | Mean roof height | (ft) | 11 | [14 empty] | Mean roof height | (ft) | 11 | [14 empty] | Mean roof height | (ft) | 11 | [14 empty] | Mean roof height | (ft) | 11
CASES | [16 empty] | CASES | [16 empty] | CASES | [16 empty] | CASES | [16 empty] | CASES | [16 empty] | CASES | [16 empty] | CASES | [16 empty] | CASES
Define cases | [16 empty] | Define cases | [16 empty] | Define cases | [16 empty] | Define cases | [16 empty] | Define cases | [16 empty] | Define cases | [16 empty] | Define cases | [16 empty] | Define cases
| Wind direction (X or Y) | X | [15 empty] | Wind direction (X or Y) | X | [15 empty] | Wind direction (X or Y) | X | [15 empty] | Wind direction (X or Y) | X | [15 empty] | Wind direction (X or Y) | Y | [15 empty] | Wind direction (X or Y) | Y | [15 empty] | Wind direction (X or Y) | Y | [15 empty] | Wind direction (X or Y) | Y
| Wind speed (mph) from Step 2 | 20 | [15 empty] | Wind speed (mph) from Step 2 | 20 | [15 empty] | Wind speed (mph) from Step 2 | 20 | [15 empty] | Wind speed (mph) from Step 2 | 20 | [15 empty] | Wind speed (mph) from Step 2 | 20 | [15 empty] | Wind speed (mph) from Step 2 | 20 | [15 empty] | Wind speed (mph) from Step 2 | 20 | [15 empty] | Wind speed (mph) from Step 2 | 20
| Case 1 or 2 for Internal pressure coefficient (Gcpi) in Step 3 | 1 | [15 empty] | Case 1 or 2 for Internal pressure coefficient (Gcpi) in Step 3 | 1 | [15 empty] | Case 1 or 2 for Internal pressure coefficient (Gcpi) in Step 3 | 2 | [15 empty] | Case 1 or 2 for Internal pressure coefficient (Gcpi) in Step 3 | 2 | [15 empty] | Case 1 or 2 for Internal pressure coefficient (Gcpi) in Step 3 | 1 | [15 empty] | Case 1 or 2 for Internal pressure coefficient (Gcpi) in Step 3 | 1 | [15 empty] | Case 1 or 2 for Internal pressure coefficient (Gcpi) in Step 3 | 2 | [15 empty] | Case 1 or 2 for Internal pressure coefficient (Gcpi) in Step 3 | 2
| Load case for Cp (A or B, both must be tested) in Step 6 | A | [15 empty] | Load case for Cp (A or B, both must be tested) in Step 6 | B | [15 empty] | Load case for Cp (A or B, both must be tested) in Step 6 | A | [15 empty] | Load case for Cp (A or B, both must be tested) in Step 6 | B | [15 empty] | Load case for Cp (A or B, both must be tested) in Step 6 | A | [15 empty] | Load case for Cp (A or B, both must be tested) in Step 6 | B | [15 empty] | Load case for Cp (A or B, both must be tested) in Step 6 | A | [15 empty] | Load case for Cp (A or B, both must be tested) in Step 6 | B
| Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [14 empty] | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [14 empty] | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [14 empty] | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [14 empty] | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [14 empty] | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [14 empty] | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3) | [14 empty] | Wind flow (1 = clear, 2, 3 = obstructed) | 1 | Clear (=1), partially obstructed (=2) or completely obstructed (=3)
|  | D | This is used at 2 locations: exposure category for Kz (Step 4) | [15 empty] | D | This is used at 2 locations: exposure category for Kz (Step 4) | [15 empty] | D | This is used at 2 locations: exposure category for Kz (Step 4) | [15 empty] | D | This is used at 2 locations: exposure category for Kz (Step 4) | [15 empty] | D | This is used at 2 locations: exposure category for Kz (Step 4) | [15 empty] | D | This is used at 2 locations: exposure category for Kz (Step 4) | [15 empty] | D | This is used at 2 locations: exposure category for Kz (Step 4) | [15 empty] | D | This is used at 2 locations: exposure category for Kz (Step 4)
|  |  | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [16 empty] | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [16 empty] | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [16 empty] | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [16 empty] | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [16 empty] | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [16 empty] | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach) | [16 empty] | Clear wind flow denotes unobstructed wind flow with no blockage (e.g., plain, grass land, beach)
|  |  | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [16 empty] | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [16 empty] | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [16 empty] | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [16 empty] | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [16 empty] | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [16 empty] | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. | [16 empty] | Partially obstructed wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%.
|  |  | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [16 empty] | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [16 empty] | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [16 empty] | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [16 empty] | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [16 empty] | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [16 empty] | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff) | [16 empty] | Completely obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage (e.g., urban environment, high dense vegetation, high cliff)
|  |  | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [16 empty] | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [16 empty] | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [16 empty] | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [16 empty] | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [16 empty] | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [16 empty] | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively | [16 empty] | ATTENTION: For Kz, the code 1/2/3 is replaced with D/C/B, respectively
| Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [14 empty] | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [14 empty] | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [14 empty] | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [14 empty] | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [14 empty] | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [14 empty] | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [14 empty] | Risk Category (I, II, III, IV) | I | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail.
|  |  | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings.
|  |  | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls.
|  |  | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation.
1 - RISK | [16 empty] | 1 - RISK | [16 empty] | 1 - RISK | [16 empty] | 1 - RISK | [16 empty] | 1 - RISK | [16 empty] | 1 - RISK | [16 empty] | 1 - RISK | [16 empty] | 1 - RISK
Step 1: Determine risk category of building or other structure, see Table 1.5-1 | [16 empty] | Step 1: Determine risk category of building or other structure, see Table 1.5-1 | [16 empty] | Step 1: Determine risk category of building or other structure, see Table 1.5-1 | [16 empty] | Step 1: Determine risk category of building or other structure, see Table 1.5-1 | [16 empty] | Step 1: Determine risk category of building or other structure, see Table 1.5-1 | [16 empty] | Step 1: Determine risk category of building or other structure, see Table 1.5-1 | [16 empty] | Step 1: Determine risk category of building or other structure, see Table 1.5-1 | [16 empty] | Step 1: Determine risk category of building or other structure, see Table 1.5-1
| Risk Category (Section C1.5.1) | I, II, III, IV | I | [14 empty] | Risk Category (Section C1.5.1) | I, II, III, IV | I | [14 empty] | Risk Category (Section C1.5.1) | I, II, III, IV | I | [14 empty] | Risk Category (Section C1.5.1) | I, II, III, IV | I | [14 empty] | Risk Category (Section C1.5.1) | I, II, III, IV | I | [14 empty] | Risk Category (Section C1.5.1) | I, II, III, IV | I | [14 empty] | Risk Category (Section C1.5.1) | I, II, III, IV | I | [14 empty] | Risk Category (Section C1.5.1) | I, II, III, IV | I
| Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [16 empty] | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [16 empty] | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [16 empty] | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [16 empty] | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [16 empty] | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [16 empty] | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail. | [16 empty] | Risk Category I structures generally encompass buildings and structures that normally are unoccupied and that would result in negligible risk to the public should they fail.
| Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings. | [16 empty] | Risk Category II includes the vast majority of structures, including most residential, commercial, and industrial buildings.
| Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls. | [16 empty] | Risk Category III includes buildings and structures that house a large number of persons in one place, such as theaters and lecture halls.
| Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation. | [16 empty] | Risk Category IV has traditionally included structures the failure of which would inhibit the availability of essential community services necessary to cope with an emergency situation.
| Assume Risk Category I because we assume that tents will be evacuated in case of high winds or upcoming storms. | [16 empty] | Assume Risk Category I because we assume that tents will be evacuated in case of high winds or upcoming storms. | [16 empty] | Assume Risk Category I because we assume that tents will be evacuated in case of high winds or upcoming storms. | [16 empty] | Assume Risk Category I because we assume that tents will be evacuated in case of high winds or upcoming storms. | [16 empty] | Assume Risk Category I because we assume that tents will be evacuated in case of high winds or upcoming storms. | [16 empty] | Assume Risk Category I because we assume that tents will be evacuated in case of high winds or upcoming storms. | [16 empty] | Assume Risk Category I because we assume that tents will be evacuated in case of high winds or upcoming storms. | [16 empty] | Assume Risk Category I because we assume that tents will be evacuated in case of high winds or upcoming storms.
| The Risk Category is used to identify Basic Wind Speed based on location | [16 empty] | The Risk Category is used to identify Basic Wind Speed based on location | [16 empty] | The Risk Category is used to identify Basic Wind Speed based on location | [16 empty] | The Risk Category is used to identify Basic Wind Speed based on location | [16 empty] | The Risk Category is used to identify Basic Wind Speed based on location | [16 empty] | The Risk Category is used to identify Basic Wind Speed based on location | [16 empty] | The Risk Category is used to identify Basic Wind Speed based on location | [16 empty] | The Risk Category is used to identify Basic Wind Speed based on location
| Skip this step since wind speed will probably be set to much lower value by member (e.g., 70 mph) | [16 empty] | Skip this step since wind speed will probably be set to much lower value by member (e.g., 70 mph) | [16 empty] | Skip this step since wind speed will probably be set to much lower value by member (e.g., 70 mph) | [16 empty] | Skip this step since wind speed will probably be set to much lower value by member (e.g., 70 mph) | [16 empty] | Skip this step since wind speed will probably be set to much lower value by member (e.g., 70 mph) | [16 empty] | Skip this step since wind speed will probably be set to much lower value by member (e.g., 70 mph) | [16 empty] | Skip this step since wind speed will probably be set to much lower value by member (e.g., 70 mph) | [16 empty] | Skip this step since wind speed will probably be set to much lower value by member (e.g., 70 mph)
| It is assumed that the Basic Wind Speed is the actual wind speed. | [16 empty] | It is assumed that the Basic Wind Speed is the actual wind speed. | [16 empty] | It is assumed that the Basic Wind Speed is the actual wind speed. | [16 empty] | It is assumed that the Basic Wind Speed is the actual wind speed. | [16 empty] | It is assumed that the Basic Wind Speed is the actual wind speed. | [16 empty] | It is assumed that the Basic Wind Speed is the actual wind speed. | [16 empty] | It is assumed that the Basic Wind Speed is the actual wind speed. | [16 empty] | It is assumed that the Basic Wind Speed is the actual wind speed.
2 - WIND SPEED | [16 empty] | 2 - WIND SPEED | [16 empty] | 2 - WIND SPEED | [16 empty] | 2 - WIND SPEED | [16 empty] | 2 - WIND SPEED | [16 empty] | 2 - WIND SPEED | [16 empty] | 2 - WIND SPEED | [16 empty] | 2 - WIND SPEED
Step 2: Determine the basic wind speed, V, for the applicable risk category, see Figure 26.5-1A, B, or C | [16 empty] | Step 2: Determine the basic wind speed, V, for the applicable risk category, see Figure 26.5-1A, B, or C | [16 empty] | Step 2: Determine the basic wind speed, V, for the applicable risk category, see Figure 26.5-1A, B, or C | [16 empty] | Step 2: Determine the basic wind speed, V, for the applicable risk category, see Figure 26.5-1A, B, or C | [16 empty] | Step 2: Determine the basic wind speed, V, for the applicable risk category, see Figure 26.5-1A, B, or C | [16 empty] | Step 2: Determine the basic wind speed, V, for the applicable risk category, see Figure 26.5-1A, B, or C | [16 empty] | Step 2: Determine the basic wind speed, V, for the applicable risk category, see Figure 26.5-1A, B, or C | [16 empty] | Step 2: Determine the basic wind speed, V, for the applicable risk category, see Figure 26.5-1A, B, or C
| From Step 1: | [16 empty] | From Step 1: | [16 empty] | From Step 1: | [16 empty] | From Step 1: | [16 empty] | From Step 1: | [16 empty] | From Step 1: | [16 empty] | From Step 1: | [16 empty] | From Step 1:
| Risk Category | I, II, III, IV | I | [14 empty] | Risk Category | I, II, III, IV | I | [14 empty] | Risk Category | I, II, III, IV | I | [14 empty] | Risk Category | I, II, III, IV | I | [14 empty] | Risk Category | I, II, III, IV | I | [14 empty] | Risk Category | I, II, III, IV | I | [14 empty] | Risk Category | I, II, III, IV | I | [14 empty] | Risk Category | I, II, III, IV | I
| Basic wind speed (26.5) (mph) | V (mph) | 20 | [14 empty] | Basic wind speed (26.5) (mph) | V (mph) | 20 | [14 empty] | Basic wind speed (26.5) (mph) | V (mph) | 20 | [14 empty] | Basic wind speed (26.5) (mph) | V (mph) | 20 | [14 empty] | Basic wind speed (26.5) (mph) | V (mph) | 20 | [14 empty] | Basic wind speed (26.5) (mph) | V (mph) | 20 | [14 empty] | Basic wind speed (26.5) (mph) | V (mph) | 20 | [14 empty] | Basic wind speed (26.5) (mph) | V (mph) | 20
| The graphs show that the wind speed should be at least 105 mph but it is expected that the members will choose a much smaller wind speed. | [16 empty] | The graphs show that the wind speed should be at least 105 mph but it is expected that the members will choose a much smaller wind speed. | [16 empty] | The graphs show that the wind speed should be at least 105 mph but it is expected that the members will choose a much smaller wind speed. | [16 empty] | The graphs show that the wind speed should be at least 105 mph but it is expected that the members will choose a much smaller wind speed. | [16 empty] | The graphs show that the wind speed should be at least 105 mph but it is expected that the members will choose a much smaller wind speed. | [16 empty] | The graphs show that the wind speed should be at least 105 mph but it is expected that the members will choose a much smaller wind speed. | [16 empty] | The graphs show that the wind speed should be at least 105 mph but it is expected that the members will choose a much smaller wind speed. | [16 empty] | The graphs show that the wind speed should be at least 105 mph but it is expected that the members will choose a much smaller wind speed.
| The basic wind speed, V, is used in step 4 to calculate the velocity pressure qz and qh | [16 empty] | The basic wind speed, V, is used in step 4 to calculate the velocity pressure qz and qh | [16 empty] | The basic wind speed, V, is used in step 4 to calculate the velocity pressure qz and qh | [16 empty] | The basic wind speed, V, is used in step 4 to calculate the velocity pressure qz and qh | [16 empty] | The basic wind speed, V, is used in step 4 to calculate the velocity pressure qz and qh | [16 empty] | The basic wind speed, V, is used in step 4 to calculate the velocity pressure qz and qh | [16 empty] | The basic wind speed, V, is used in step 4 to calculate the velocity pressure qz and qh | [16 empty] | The basic wind speed, V, is used in step 4 to calculate the velocity pressure qz and qh
3 - MISCELLANEOUS | [16 empty] | 3 - MISCELLANEOUS | [16 empty] | 3 - MISCELLANEOUS | [16 empty] | 3 - MISCELLANEOUS | [16 empty] | 3 - MISCELLANEOUS | [16 empty] | 3 - MISCELLANEOUS | [16 empty] | 3 - MISCELLANEOUS | [16 empty] | 3 - MISCELLANEOUS
Step 3: Determine wind load parameters: | [16 empty] | Step 3: Determine wind load parameters: | [16 empty] | Step 3: Determine wind load parameters: | [16 empty] | Step 3: Determine wind load parameters: | [16 empty] | Step 3: Determine wind load parameters: | [16 empty] | Step 3: Determine wind load parameters: | [16 empty] | Step 3: Determine wind load parameters: | [16 empty] | Step 3: Determine wind load parameters:
| Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1
| Exposure category, see Section 26.7 | [16 empty] | Exposure category, see Section 26.7 | [16 empty] | Exposure category, see Section 26.7 | [16 empty] | Exposure category, see Section 26.7 | [16 empty] | Exposure category, see Section 26.7 | [16 empty] | Exposure category, see Section 26.7 | [16 empty] | Exposure category, see Section 26.7 | [16 empty] | Exposure category, see Section 26.7
| Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1
| Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9
| Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10
| Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1
Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1 | [16 empty] | Wind directionality factor, Kd , see Section 26.6 and Table 26.6-1
| Wind directionality factor (26.6) | Kd | 1 | Table 26.6.1 | [13 empty] | Wind directionality factor (26.6) | Kd | 1 | Table 26.6.1 | [13 empty] | Wind directionality factor (26.6) | Kd | 1 | Table 26.6.1 | [13 empty] | Wind directionality factor (26.6) | Kd | 1 | Table 26.6.1 | [13 empty] | Wind directionality factor (26.6) | Kd | 1 | Table 26.6.1 | [13 empty] | Wind directionality factor (26.6) | Kd | 1 | Table 26.6.1 | [13 empty] | Wind directionality factor (26.6) | Kd | 1 | Table 26.6.1 | [13 empty] | Wind directionality factor (26.6) | Kd | 1 | Table 26.6.1
Used Kd = 1 as opposed to 0.85 because code says to use 0.85 when loads are accumulated as in sections 2.3 and 2.4 of the code.
Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1 | [16 empty] | Topographic factor, Kzt, see Section 26.8 and Figure 26.8-1
| Topographic factor (26.8.2) | Kzt | 1 | Check potential variations of Kzt | [13 empty] | Topographic factor (26.8.2) | Kzt | 1 | Check potential variations of Kzt | [13 empty] | Topographic factor (26.8.2) | Kzt | 1 | Check potential variations of Kzt | [13 empty] | Topographic factor (26.8.2) | Kzt | 1 | Check potential variations of Kzt | [13 empty] | Topographic factor (26.8.2) | Kzt | 1 | Check potential variations of Kzt | [13 empty] | Topographic factor (26.8.2) | Kzt | 1 | Check potential variations of Kzt | [13 empty] | Topographic factor (26.8.2) | Kzt | 1 | Check potential variations of Kzt | [13 empty] | Topographic factor (26.8.2) | Kzt | 1 | Check potential variations of Kzt
Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9 | [16 empty] | Gust-effect factor, G, see Section 26.9
| Term 2: G (Sect. 26.9.1 for rigid, 26.9.5 for flexible) | G | 0.85 | [14 empty] | Term 2: G (Sect. 26.9.1 for rigid, 26.9.5 for flexible) | G | 0.85 | [14 empty] | Term 2: G (Sect. 26.9.1 for rigid, 26.9.5 for flexible) | G | 0.85 | [14 empty] | Term 2: G (Sect. 26.9.1 for rigid, 26.9.5 for flexible) | G | 0.85 | [14 empty] | Term 2: G (Sect. 26.9.1 for rigid, 26.9.5 for flexible) | G | 0.85 | [14 empty] | Term 2: G (Sect. 26.9.1 for rigid, 26.9.5 for flexible) | G | 0.85 | [14 empty] | Term 2: G (Sect. 26.9.1 for rigid, 26.9.5 for flexible) | G | 0.85 | [14 empty] | Term 2: G (Sect. 26.9.1 for rigid, 26.9.5 for flexible) | G | 0.85
Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10 | [16 empty] | Enclosure classification, see Section 26.10
| For the purpose of determining internal pressure | [16 empty] | For the purpose of determining internal pressure | [16 empty] | For the purpose of determining internal pressure | [16 empty] | For the purpose of determining internal pressure | [16 empty] | For the purpose of determining internal pressure | [16 empty] | For the purpose of determining internal pressure | [16 empty] | For the purpose of determining internal pressure | [16 empty] | For the purpose of determining internal pressure
| coefficients, all buildings shall be classified as enclosed, | [16 empty] | coefficients, all buildings shall be classified as enclosed, | [16 empty] | coefficients, all buildings shall be classified as enclosed, | [16 empty] | coefficients, all buildings shall be classified as enclosed, | [16 empty] | coefficients, all buildings shall be classified as enclosed, | [16 empty] | coefficients, all buildings shall be classified as enclosed, | [16 empty] | coefficients, all buildings shall be classified as enclosed, | [16 empty] | coefficients, all buildings shall be classified as enclosed,
| partially enclosed, or open as defined in Section 26.2. | [16 empty] | partially enclosed, or open as defined in Section 26.2. | [16 empty] | partially enclosed, or open as defined in Section 26.2. | [16 empty] | partially enclosed, or open as defined in Section 26.2. | [16 empty] | partially enclosed, or open as defined in Section 26.2. | [16 empty] | partially enclosed, or open as defined in Section 26.2. | [16 empty] | partially enclosed, or open as defined in Section 26.2. | [16 empty] | partially enclosed, or open as defined in Section 26.2.
Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1 | [16 empty] | Internal pressure coefficient, (GCpi), see Section 26.11 and Table 26.11-1
| Two cases shall be considered | [16 empty] | Two cases shall be considered | [16 empty] | Two cases shall be considered | [16 empty] | Two cases shall be considered | [16 empty] | Two cases shall be considered | [16 empty] | Two cases shall be considered | [16 empty] | Two cases shall be considered | [16 empty] | Two cases shall be considered
| For all surfaces (Walls and Roof) | [16 empty] | For all surfaces (Walls and Roof) | [16 empty] | For all surfaces (Walls and Roof) | [16 empty] | For all surfaces (Walls and Roof) | [16 empty] | For all surfaces (Walls and Roof) | [16 empty] | For all surfaces (Walls and Roof) | [16 empty] | For all surfaces (Walls and Roof) | [16 empty] | For all surfaces (Walls and Roof)
|  |  | Case 1 | Case 2 | [15 empty] | Case 1 | Case 2 | [15 empty] | Case 1 | Case 2 | [15 empty] | Case 1 | Case 2 | [15 empty] | Case 1 | Case 2 | [15 empty] | Case 1 | Case 2 | [15 empty] | Case 1 | Case 2 | [15 empty] | Case 1 | Case 2
| Open | GCpi | 0 | 0 | Plus and minus signs signify pressures acting toward | [12 empty] | Open | GCpi | 0 | 0 | Plus and minus signs signify pressures acting toward | [12 empty] | Open | GCpi | 0 | 0 | Plus and minus signs signify pressures acting toward | [12 empty] | Open | GCpi | 0 | 0 | Plus and minus signs signify pressures acting toward | [12 empty] | Open | GCpi | 0 | 0 | Plus and minus signs signify pressures acting toward | [12 empty] | Open | GCpi | 0 | 0 | Plus and minus signs signify pressures acting toward | [12 empty] | Open | GCpi | 0 | 0 | Plus and minus signs signify pressures acting toward | [12 empty] | Open | GCpi | 0 | 0 | Plus and minus signs signify pressures acting toward
| Partially enclosed | GCpi | 0.55 | -0.55 | & away from the internal surfaces, respectively. | [12 empty] | Partially enclosed | GCpi | 0.55 | -0.55 | & away from the internal surfaces, respectively. | [12 empty] | Partially enclosed | GCpi | 0.55 | -0.55 | & away from the internal surfaces, respectively. | [12 empty] | Partially enclosed | GCpi | 0.55 | -0.55 | & away from the internal surfaces, respectively. | [12 empty] | Partially enclosed | GCpi | 0.55 | -0.55 | & away from the internal surfaces, respectively. | [12 empty] | Partially enclosed | GCpi | 0.55 | -0.55 | & away from the internal surfaces, respectively. | [12 empty] | Partially enclosed | GCpi | 0.55 | -0.55 | & away from the internal surfaces, respectively. | [12 empty] | Partially enclosed | GCpi | 0.55 | -0.55 | & away from the internal surfaces, respectively.
| Case | 1 | [15 empty] | Case | 1 | [15 empty] | Case | 2 | [15 empty] | Case | 2 | [15 empty] | Case | 1 | [15 empty] | Case | 1 | [15 empty] | Case | 2 | [15 empty] | Case | 2
| Open | GCpi | 0 | [14 empty] | Open | GCpi | 0 | [14 empty] | Open | GCpi |  | 0 | [13 empty] | Open | GCpi |  | 0 | [13 empty] | Open | GCpi | 0 | [14 empty] | Open | GCpi | 0 | [14 empty] | Open | GCpi |  | 0 | [13 empty] | Open | GCpi |  | 0
| Partially enclosed | GCpi | 0.55 | [14 empty] | Partially enclosed | GCpi | 0.55 | [14 empty] | Partially enclosed | GCpi |  | -0.55 | [13 empty] | Partially enclosed | GCpi |  | -0.55 | [13 empty] | Partially enclosed | GCpi | 0.55 | [14 empty] | Partially enclosed | GCpi | 0.55 | [14 empty] | Partially enclosed | GCpi |  | -0.55 | [13 empty] | Partially enclosed | GCpi |  | -0.55
| OPEN | GCpi | 0 | [14 empty] | OPEN | GCpi | 0 | [14 empty] | OPEN | GCpi | 0 | [14 empty] | OPEN | GCpi | 0 | [14 empty] | OPEN | GCpi | 0 | [14 empty] | OPEN | GCpi | 0 | [14 empty] | OPEN | GCpi | 0 | [14 empty] | OPEN | GCpi | 0
| PARTIALLY ENCLOSED | GCpi | 0.55 | [14 empty] | PARTIALLY ENCLOSED | GCpi | 0.55 | [14 empty] | PARTIALLY ENCLOSED | GCpi | -0.55 | [14 empty] | PARTIALLY ENCLOSED | GCpi | -0.55 | [14 empty] | PARTIALLY ENCLOSED | GCpi | 0.55 | [14 empty] | PARTIALLY ENCLOSED | GCpi | 0.55 | [14 empty] | PARTIALLY ENCLOSED | GCpi | -0.55 | [14 empty] | PARTIALLY ENCLOSED | GCpi | -0.55
4 - Kz | [16 empty] | 4 - Kz | [16 empty] | 4 - Kz | [16 empty] | 4 - Kz | [16 empty] | 4 - Kz | [16 empty] | 4 - Kz | [16 empty] | 4 - Kz | [16 empty] | 4 - Kz
Step 4: Determine velocity pressure exposure coefficient, Kz or Kh, see Table 27.3-1 | [16 empty] | Step 4: Determine velocity pressure exposure coefficient, Kz or Kh, see Table 27.3-1 | [16 empty] | Step 4: Determine velocity pressure exposure coefficient, Kz or Kh, see Table 27.3-1 | [16 empty] | Step 4: Determine velocity pressure exposure coefficient, Kz or Kh, see Table 27.3-1 | [16 empty] | Step 4: Determine velocity pressure exposure coefficient, Kz or Kh, see Table 27.3-1 | [16 empty] | Step 4: Determine velocity pressure exposure coefficient, Kz or Kh, see Table 27.3-1 | [16 empty] | Step 4: Determine velocity pressure exposure coefficient, Kz or Kh, see Table 27.3-1 | [16 empty] | Step 4: Determine velocity pressure exposure coefficient, Kz or Kh, see Table 27.3-1
|  |  | Exposure category | [16 empty] | Exposure category | [16 empty] | Exposure category | [16 empty] | Exposure category | [16 empty] | Exposure category | [12 empty] | Exposure category |  |  |  | Exposure category | [11 empty] | Exposure category |  |  |  |  | Exposure category | [16 empty] | Exposure category
|  |  | B | C | D | [14 empty] | B | C | D | [14 empty] | B | C | D | [14 empty] | B | C | D | [14 empty] | B | C | D | [14 empty] | B | C | D | [14 empty] | B | C | D | [14 empty] | B | C | D
| Table 26.9.1 | alpha | 7 | 9.5 | 11.5 | [12 empty] | Table 26.9.1 | alpha | 7 | 9.5 | 11.5 | [12 empty] | Table 26.9.1 | alpha | 7 | 9.5 | 11.5 | [12 empty] | Table 26.9.1 | alpha | 7 | 9.5 | 11.5 | [12 empty] | Table 26.9.1 | alpha | 7 | 9.5 | 11.5 | [12 empty] | Table 26.9.1 | alpha | 7 | 9.5 | 11.5 | [12 empty] | Table 26.9.1 | alpha | 7 | 9.5 | 11.5 | [12 empty] | Table 26.9.1 | alpha | 7 | 9.5 | 11.5
| Table 26.9.1 | zg (ft) | 1200 | 900 | 700 | [12 empty] | Table 26.9.1 | zg (ft) | 1200 | 900 | 700 | [12 empty] | Table 26.9.1 | zg (ft) | 1200 | 900 | 700 | [12 empty] | Table 26.9.1 | zg (ft) | 1200 | 900 | 700 | [12 empty] | Table 26.9.1 | zg (ft) | 1200 | 900 | 700 | [12 empty] | Table 26.9.1 | zg (ft) | 1200 | 900 | 700 | [12 empty] | Table 26.9.1 | zg (ft) | 1200 | 900 | 700 | [12 empty] | Table 26.9.1 | zg (ft) | 1200 | 900 | 700
| z = 0 ft | z (ft) | 0 | 0 | 0 | [12 empty] | z = 0 ft | z (ft) | 0 | 0 | 0 | [12 empty] | z = 0 ft | z (ft) | 0 | 0 | 0 | [12 empty] | z = 0 ft | z (ft) | 0 | 0 | 0 | [12 empty] | z = 0 ft | z (ft) | 0 | 0 | 0 | [12 empty] | z = 0 ft | z (ft) | 0 | 0 | 0 | [12 empty] | z = 0 ft | z (ft) | 0 | 0 | 0 | [12 empty] | z = 0 ft | z (ft) | 0 | 0 | 0
| Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302
| z = 15 ft | z (ft) | 15 | 15 | 15 | [12 empty] | z = 15 ft | z (ft) | 15 | 15 | 15 | [12 empty] | z = 15 ft | z (ft) | 15 | 15 | 15 | [12 empty] | z = 15 ft | z (ft) | 15 | 15 | 15 | [12 empty] | z = 15 ft | z (ft) | 15 | 15 | 15 | [12 empty] | z = 15 ft | z (ft) | 15 | 15 | 15 | [12 empty] | z = 15 ft | z (ft) | 15 | 15 | 15 | [12 empty] | z = 15 ft | z (ft) | 15 | 15 | 15
| Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302
| z = H | z (ft) | 8 | 8 | 8 | [12 empty] | z = H | z (ft) | 8 | 8 | 8 | [12 empty] | z = H | z (ft) | 8 | 8 | 8 | [12 empty] | z = H | z (ft) | 8 | 8 | 8 | [12 empty] | z = H | z (ft) | 8 | 8 | 8 | [12 empty] | z = H | z (ft) | 8 | 8 | 8 | [12 empty] | z = H | z (ft) | 8 | 8 | 8 | [12 empty] | z = H | z (ft) | 8 | 8 | 8
| Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302
| z = RMH | h (ft) | 11 | 11 | 11 | [12 empty] | z = RMH | h (ft) | 11 | 11 | 11 | [12 empty] | z = RMH | h (ft) | 11 | 11 | 11 | [12 empty] | z = RMH | h (ft) | 11 | 11 | 11 | [12 empty] | z = RMH | h (ft) | 11 | 11 | 11 | [12 empty] | z = RMH | h (ft) | 11 | 11 | 11 | [12 empty] | z = RMH | h (ft) | 11 | 11 | 11 | [12 empty] | z = RMH | h (ft) | 11 | 11 | 11
| Velocity pressure exposure coef at MRH (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302 | [12 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz | 0.57472 | 0.84888 | 1.0302
| Exposure category from Step 3 | D | [15 empty] | Exposure category from Step 3 | D | [15 empty] | Exposure category from Step 3 | D | [15 empty] | Exposure category from Step 3 | D | [15 empty] | Exposure category from Step 3 | D | [15 empty] | Exposure category from Step 3 | D | [15 empty] | Exposure category from Step 3 | D | [15 empty] | Exposure category from Step 3 | D
| Table 26.9.1 | alpha |  |  | 11.5 | [12 empty] | Table 26.9.1 | alpha |  |  | 11.5 | [12 empty] | Table 26.9.1 | alpha |  |  | 11.5 | [12 empty] | Table 26.9.1 | alpha |  |  | 11.5 | [12 empty] | Table 26.9.1 | alpha |  |  | 11.5 | [12 empty] | Table 26.9.1 | alpha |  |  | 11.5 | [12 empty] | Table 26.9.1 | alpha |  |  | 11.5 | [12 empty] | Table 26.9.1 | alpha |  |  | 11.5
| Table 26.9.1 | zg (ft) |  |  | 700 | [12 empty] | Table 26.9.1 | zg (ft) |  |  | 700 | [12 empty] | Table 26.9.1 | zg (ft) |  |  | 700 | [12 empty] | Table 26.9.1 | zg (ft) |  |  | 700 | [12 empty] | Table 26.9.1 | zg (ft) |  |  | 700 | [12 empty] | Table 26.9.1 | zg (ft) |  |  | 700 | [12 empty] | Table 26.9.1 | zg (ft) |  |  | 700 | [12 empty] | Table 26.9.1 | zg (ft) |  |  | 700
| z = 0 ft | z (ft) |  |  | 0 | 0 | [11 empty] | z = 0 ft | z (ft) |  |  | 0 | 0 | [11 empty] | z = 0 ft | z (ft) |  |  | 0 | 0 | [11 empty] | z = 0 ft | z (ft) |  |  | 0 | 0 | [11 empty] | z = 0 ft | z (ft) |  |  | 0 | 0 | [11 empty] | z = 0 ft | z (ft) |  |  | 0 | 0 | [11 empty] | z = 0 ft | z (ft) |  |  | 0 | 0 | [11 empty] | z = 0 ft | z (ft) |  |  | 0 | 0
| Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302
| z = 15 ft | z (ft) |  |  | 15 | 15 | [11 empty] | z = 15 ft | z (ft) |  |  | 15 | 15 | [11 empty] | z = 15 ft | z (ft) |  |  | 15 | 15 | [11 empty] | z = 15 ft | z (ft) |  |  | 15 | 15 | [11 empty] | z = 15 ft | z (ft) |  |  | 15 | 15 | [11 empty] | z = 15 ft | z (ft) |  |  | 15 | 15 | [11 empty] | z = 15 ft | z (ft) |  |  | 15 | 15 | [11 empty] | z = 15 ft | z (ft) |  |  | 15 | 15
| Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302
| z = H | z (ft) |  |  | 8 | 8 | [11 empty] | z = H | z (ft) |  |  | 8 | 8 | [11 empty] | z = H | z (ft) |  |  | 8 | 8 | [11 empty] | z = H | z (ft) |  |  | 8 | 8 | [11 empty] | z = H | z (ft) |  |  | 8 | 8 | [11 empty] | z = H | z (ft) |  |  | 8 | 8 | [11 empty] | z = H | z (ft) |  |  | 8 | 8 | [11 empty] | z = H | z (ft) |  |  | 8 | 8
| Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef (27.3.1) | Kz |  |  | 1.0302 | 1.0302
| z = RMH = h | h (ft) |  |  | 11 | 11 | [11 empty] | z = RMH = h | h (ft) |  |  | 11 | 11 | [11 empty] | z = RMH = h | h (ft) |  |  | 11 | 11 | [11 empty] | z = RMH = h | h (ft) |  |  | 11 | 11 | [11 empty] | z = RMH = h | h (ft) |  |  | 11 | 11 | [11 empty] | z = RMH = h | h (ft) |  |  | 11 | 11 | [11 empty] | z = RMH = h | h (ft) |  |  | 11 | 11 | [11 empty] | z = RMH = h | h (ft) |  |  | 11 | 11
| Velocity pressure exposure coef at MRH (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz |  |  | 1.0302 | 1.0302 | [11 empty] | Velocity pressure exposure coef at MRH (27.3.1) | Kz |  |  | 1.0302 | 1.0302
|  | z | Kz, Kh | [15 empty] | z | Kz, Kh | [15 empty] | z | Kz, Kh | [15 empty] | z | Kz, Kh | [15 empty] | z | Kz, Kh | [15 empty] | z | Kz, Kh | [15 empty] | z | Kz, Kh | [15 empty] | z | Kz, Kh
| z = 0 ft | 0 | 1.0302 | Kz | [13 empty] | z = 0 ft | 0 | 1.0302 | Kz | [13 empty] | z = 0 ft | 0 | 1.0302 | Kz | [13 empty] | z = 0 ft | 0 | 1.0302 | Kz | [13 empty] | z = 0 ft | 0 | 1.0302 | Kz | [13 empty] | z = 0 ft | 0 | 1.0302 | Kz | [13 empty] | z = 0 ft | 0 | 1.0302 | Kz | [13 empty] | z = 0 ft | 0 | 1.0302 | Kz
| z = 15 ft | 15 | 1.0302 | Kz | [13 empty] | z = 15 ft | 15 | 1.0302 | Kz | [13 empty] | z = 15 ft | 15 | 1.0302 | Kz | [13 empty] | z = 15 ft | 15 | 1.0302 | Kz | [13 empty] | z = 15 ft | 15 | 1.0302 | Kz | [13 empty] | z = 15 ft | 15 | 1.0302 | Kz | [13 empty] | z = 15 ft | 15 | 1.0302 | Kz | [13 empty] | z = 15 ft | 15 | 1.0302 | Kz
| z = H | 8 | 1.0302 | Kz | [13 empty] | z = H | 8 | 1.0302 | Kz | [13 empty] | z = H | 8 | 1.0302 | Kz | [13 empty] | z = H | 8 | 1.0302 | Kz | [13 empty] | z = H | 8 | 1.0302 | Kz | [13 empty] | z = H | 8 | 1.0302 | Kz | [13 empty] | z = H | 8 | 1.0302 | Kz | [13 empty] | z = H | 8 | 1.0302 | Kz
| z = RMH = h | 11 | 1.0302 | Kh | [13 empty] | z = RMH = h | 11 | 1.0302 | Kh | [13 empty] | z = RMH = h | 11 | 1.0302 | Kh | [13 empty] | z = RMH = h | 11 | 1.0302 | Kh | [13 empty] | z = RMH = h | 11 | 1.0302 | Kh | [13 empty] | z = RMH = h | 11 | 1.0302 | Kh | [13 empty] | z = RMH = h | 11 | 1.0302 | Kh | [13 empty] | z = RMH = h | 11 | 1.0302 | Kh
5 - qz | [16 empty] | 5 - qz | [16 empty] | 5 - qz | [16 empty] | 5 - qz | [16 empty] | 5 - qz | [16 empty] | 5 - qz | [16 empty] | 5 - qz | [16 empty] | 5 - qz
Step 5: Determine velocity pressure qz or qh, see Eq. 27.3-1 | [16 empty] | Step 5: Determine velocity pressure qz or qh, see Eq. 27.3-1 | [16 empty] | Step 5: Determine velocity pressure qz or qh, see Eq. 27.3-1 | [16 empty] | Step 5: Determine velocity pressure qz or qh, see Eq. 27.3-1 | [16 empty] | Step 5: Determine velocity pressure qz or qh, see Eq. 27.3-1 | [16 empty] | Step 5: Determine velocity pressure qz or qh, see Eq. 27.3-1 | [16 empty] | Step 5: Determine velocity pressure qz or qh, see Eq. 27.3-1 | [16 empty] | Step 5: Determine velocity pressure qz or qh, see Eq. 27.3-1
| qz = 0.00256*Kz*Kzt*Kd*V^2 | [16 empty] | qz = 0.00256*Kz*Kzt*Kd*V^2 | [16 empty] | qz = 0.00256*Kz*Kzt*Kd*V^2 | [16 empty] | qz = 0.00256*Kz*Kzt*Kd*V^2 | [16 empty] | qz = 0.00256*Kz*Kzt*Kd*V^2 | [16 empty] | qz = 0.00256*Kz*Kzt*Kd*V^2 | [16 empty] | qz = 0.00256*Kz*Kzt*Kd*V^2 | [16 empty] | qz = 0.00256*Kz*Kzt*Kd*V^2
|  | z | qz, qh | [15 empty] | z | qz, qh | [15 empty] | z | qz, qh | [15 empty] | z | qz, qh | [15 empty] | z | qz, qh | [15 empty] | z | qz, qh | [15 empty] | z | qz, qh | [15 empty] | z | qz, qh
| z = 0 ft | 0 | 1.055 | qz | [13 empty] | z = 0 ft | 0 | 1.055 | qz | [13 empty] | z = 0 ft | 0 | 1.055 | qz | [13 empty] | z = 0 ft | 0 | 1.055 | qz | [13 empty] | z = 0 ft | 0 | 1.055 | qz | [13 empty] | z = 0 ft | 0 | 1.055 | qz | [13 empty] | z = 0 ft | 0 | 1.055 | qz | [13 empty] | z = 0 ft | 0 | 1.055 | qz
| z = 15 ft | 15 | 1.055 | qz | [13 empty] | z = 15 ft | 15 | 1.055 | qz | [13 empty] | z = 15 ft | 15 | 1.055 | qz | [13 empty] | z = 15 ft | 15 | 1.055 | qz | [13 empty] | z = 15 ft | 15 | 1.055 | qz | [13 empty] | z = 15 ft | 15 | 1.055 | qz | [13 empty] | z = 15 ft | 15 | 1.055 | qz | [13 empty] | z = 15 ft | 15 | 1.055 | qz
| z = H | 8 | 1.055 | qz | [13 empty] | z = H | 8 | 1.055 | qz | [13 empty] | z = H | 8 | 1.055 | qz | [13 empty] | z = H | 8 | 1.055 | qz | [13 empty] | z = H | 8 | 1.055 | qz | [13 empty] | z = H | 8 | 1.055 | qz | [13 empty] | z = H | 8 | 1.055 | qz | [13 empty] | z = H | 8 | 1.055 | qz
| z = RMH = h | 11 | 1.055 | qh | [13 empty] | z = RMH = h | 11 | 1.055 | qh | [13 empty] | z = RMH = h | 11 | 1.055 | qh | [13 empty] | z = RMH = h | 11 | 1.055 | qh | [13 empty] | z = RMH = h | 11 | 1.055 | qh | [13 empty] | z = RMH = h | 11 | 1.055 | qh | [13 empty] | z = RMH = h | 11 | 1.055 | qh | [13 empty] | z = RMH = h | 11 | 1.055 | qh
6.1 CN FOR OPEN | [16 empty] | 6.1 CN FOR OPEN | [16 empty] | 6.1 CN FOR OPEN | [16 empty] | 6.1 CN FOR OPEN | [16 empty] | 6.1 CN FOR OPEN | [16 empty] | 6.1 CN FOR OPEN | [16 empty] | 6.1 CN FOR OPEN | [16 empty] | 6.1 CN FOR OPEN
Step 6.1: Determine external pressure coefficient, CN for open buildings | [16 empty] | Step 6.1: Determine external pressure coefficient, CN for open buildings | [16 empty] | Step 6.1: Determine external pressure coefficient, CN for open buildings | [16 empty] | Step 6.1: Determine external pressure coefficient, CN for open buildings | [16 empty] | Step 6.1: Determine external pressure coefficient, CN for open buildings | [16 empty] | Step 6.1: Determine external pressure coefficient, CN for open buildings | [16 empty] | Step 6.1: Determine external pressure coefficient, CN for open buildings | [16 empty] | Step 6.1: Determine external pressure coefficient, CN for open buildings
| Fig. 27.4-5 for pitched roof, open building | [16 empty] | Fig. 27.4-5 for pitched roof, open building | [16 empty] | Fig. 27.4-5 for pitched roof, open building | [16 empty] | Fig. 27.4-5 for pitched roof, open building | [16 empty] | Fig. 27.4-5 for pitched roof, open building | [16 empty] | Fig. 27.4-5 for pitched roof, open building | [16 empty] | Fig. 27.4-5 for pitched roof, open building | [16 empty] | Fig. 27.4-5 for pitched roof, open building
| Fig. 27.4-7 for along-ridge/valley wind load case for pitched roof, open building | [16 empty] | Fig. 27.4-7 for along-ridge/valley wind load case for pitched roof, open building | [16 empty] | Fig. 27.4-7 for along-ridge/valley wind load case for pitched roof, open building | [16 empty] | Fig. 27.4-7 for along-ridge/valley wind load case for pitched roof, open building | [16 empty] | Fig. 27.4-7 for along-ridge/valley wind load case for pitched roof, open building | [16 empty] | Fig. 27.4-7 for along-ridge/valley wind load case for pitched roof, open building | [16 empty] | Fig. 27.4-7 for along-ridge/valley wind load case for pitched roof, open building | [16 empty] | Fig. 27.4-7 for along-ridge/valley wind load case for pitched roof, open building
| Since the wind direction is | X | [15 empty] | Since the wind direction is | X | [15 empty] | Since the wind direction is | X | [15 empty] | Since the wind direction is | X | [15 empty] | Since the wind direction is | Y | [15 empty] | Since the wind direction is | Y | [15 empty] | Since the wind direction is | Y | [15 empty] | Since the wind direction is | Y
| the non-zero ridge is | parallel | to the wind direction | [14 empty] | the non-zero ridge is | parallel | to the wind direction | [14 empty] | the non-zero ridge is | parallel | to the wind direction | [14 empty] | the non-zero ridge is | parallel | to the wind direction | [14 empty] | the non-zero ridge is | normal | to the wind direction | [14 empty] | the non-zero ridge is | normal | to the wind direction | [14 empty] | the non-zero ridge is | normal | to the wind direction | [14 empty] | the non-zero ridge is | normal | to the wind direction
| The windward and leeward roof surfaces are | +X & -X | [15 empty] | The windward and leeward roof surfaces are | +X & -X | [15 empty] | The windward and leeward roof surfaces are | +X & -X | [15 empty] | The windward and leeward roof surfaces are | +X & -X | [15 empty] | The windward and leeward roof surfaces are | +Y & -Y | [15 empty] | The windward and leeward roof surfaces are | +Y & -Y | [15 empty] | The windward and leeward roof surfaces are | +Y & -Y | [15 empty] | The windward and leeward roof surfaces are | +Y & -Y
| and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638
| The side rood surfaces are | +Y & -Y | [15 empty] | The side rood surfaces are | +Y & -Y | [15 empty] | The side rood surfaces are | +Y & -Y | [15 empty] | The side rood surfaces are | +Y & -Y | [15 empty] | The side rood surfaces are | +X & -X | [15 empty] | The side rood surfaces are | +X & -X | [15 empty] | The side rood surfaces are | +X & -X | [15 empty] | The side rood surfaces are | +X & -X
| and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993
| Tent dimension normal to wind direction | 20 | [15 empty] | Tent dimension normal to wind direction | 20 | [15 empty] | Tent dimension normal to wind direction | 20 | [15 empty] | Tent dimension normal to wind direction | 20 | [15 empty] | Tent dimension normal to wind direction | 40 | [15 empty] | Tent dimension normal to wind direction | 40 | [15 empty] | Tent dimension normal to wind direction | 40 | [15 empty] | Tent dimension normal to wind direction | 40
| Tent dimension parallel to wind direction | 40 | [15 empty] | Tent dimension parallel to wind direction | 40 | [15 empty] | Tent dimension parallel to wind direction | 40 | [15 empty] | Tent dimension parallel to wind direction | 40 | [15 empty] | Tent dimension parallel to wind direction | 20 | [15 empty] | Tent dimension parallel to wind direction | 20 | [15 empty] | Tent dimension parallel to wind direction | 20 | [15 empty] | Tent dimension parallel to wind direction | 20
| Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11
| Load case | (A or B) | A | [14 empty] | Load case | (A or B) | B | [14 empty] | Load case | (A or B) | A | [14 empty] | Load case | (A or B) | B | [14 empty] | Load case | (A or B) | A | [14 empty] | Load case | (A or B) | B | [14 empty] | Load case | (A or B) | A | [14 empty] | Load case | (A or B) | B
| Clear (=1) or obstructed (=2 or 3) wind flow | (1 or 2/3) | 1 | Clear wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. Obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage | [13 empty] | Clear (=1) or obstructed (=2 or 3) wind flow | (1 or 2/3) | 1 | Clear wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. Obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage | [13 empty] | Clear (=1) or obstructed (=2 or 3) wind flow | (1 or 2/3) | 1 | Clear wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. Obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage | [13 empty] | Clear (=1) or obstructed (=2 or 3) wind flow | (1 or 2/3) | 1 | Clear wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. Obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage | [13 empty] | Clear (=1) or obstructed (=2 or 3) wind flow | (1 or 2/3) | 1 | Clear wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. Obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage | [13 empty] | Clear (=1) or obstructed (=2 or 3) wind flow | (1 or 2/3) | 1 | Clear wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. Obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage | [13 empty] | Clear (=1) or obstructed (=2 or 3) wind flow | (1 or 2/3) | 1 | Clear wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. Obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage | [13 empty] | Clear (=1) or obstructed (=2 or 3) wind flow | (1 or 2/3) | 1 | Clear wind flow denotes relatively unobstructed wind flow with blockage less than or equal to 50%. Obstructed wind flow denotes objects below roof inhibiting wind flow with >50% blockage
| Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively.
| For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively.
| B: Horizontal dimension of building measured normal to wind direction. |  |  |  | STARTING IN VERSION main39.0 (08/14/21) | [12 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction.
| L: Horizontal dimension of building measured parallel to wind direction. |  |  |  | CHANGED THE WHOLE TABLE OF CN BY CONSIDERING BOTHER CLEAR AND OBSTRUCTED AS GENERAL CASES | [12 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction.
| h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees |  |  |  | AND ADDED A COEFFICIENT OF 1.0, 0.8, AND 0.6 FOR CLEAR, PARTIALLY OBSTRUCTED, SHELTERED LOCATION | [12 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees
| Windward and Leeward surfaces |  | Load case A |  |  |  | Load case B | [10 empty] | Windward and Leeward surfaces |  | Load case A |  |  |  | Load case B | [10 empty] | Windward and Leeward surfaces |  | Load case A |  |  |  | Load case B | [10 empty] | Windward and Leeward surfaces |  | Load case A |  |  |  | Load case B | [10 empty] | Windward and Leeward surfaces |  | Load case A |  |  |  | Load case B | [8 empty] | Load case A |  |  |  | Load case A |  |  |  | Load case B | [7 empty] | Load case A |  |  |  |  | Load case A |  |  |  | Load case B | [6 empty] | Load case A |  |  |  | Windward and Leeward surfaces |  | Load case A |  |  |  | Load case B
|  |  | Clear wind flow |  | Obstructed wind flow |  | Clear wind flow |  | Obstructed wind flow | [10 empty] | Clear wind flow |  | Obstructed wind flow |  | Clear wind flow |  | Obstructed wind flow | [10 empty] | Clear wind flow |  | Obstructed wind flow |  | Clear wind flow |  | Obstructed wind flow | [10 empty] | Clear wind flow |  | Obstructed wind flow |  | Clear wind flow |  | Obstructed wind flow | [10 empty] | Clear wind flow |  | Obstructed wind flow |  | Clear wind flow |  | Obstructed wind flow | [6 empty] | Clear wind flow |  |  |  | Clear wind flow |  | Obstructed wind flow |  | Clear wind flow |  | Obstructed wind flow | [10 empty] | Clear wind flow |  | Obstructed wind flow |  | Clear wind flow |  | Obstructed wind flow | [6 empty] | Obstructed wind flow |  |  |  | Clear wind flow |  | Obstructed wind flow |  | Clear wind flow |  | Obstructed wind flow
|  | Theta \ CN | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee |  |  |  |  | Theta \ CN | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee |  |  |  |  | Theta \ CN | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee |  |  |  |  | Theta \ CN | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee |  |  |  |  | Theta \ CN | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee |  |  |  |  | Theta \ CN | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee |  |  |  |  | Theta \ CN | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee |  |  |  |  | Theta \ CN | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee | CNWind | CNLee
|  | 0 | [8 empty] | 1.2 | 0.3 | [6 empty] | 0 | [8 empty] | -1.1 | -0.1 | [6 empty] | 0 | [8 empty] | -0.5 | -1.2 | [6 empty] | 0 | [8 empty] | -1.1 | -0.6 | [6 empty] | 0 | [8 empty] | 1.2 | 0.3 | [6 empty] | 0 | [8 empty] | -1.1 | -0.1 | [6 empty] | 0 | [8 empty] | -0.5 | -1.2 | [6 empty] | 0 | [8 empty] | -1.1 | -0.6
|  | 7.5 | [8 empty] | 1.1 | -0.3 | [6 empty] | 7.5 | [8 empty] | 0.2 | -1.2 | [6 empty] | 7.5 | [8 empty] | -1.6 | -1 | [6 empty] | 7.5 | [8 empty] | -0.9 | -1.7 | [6 empty] | 7.5 | [8 empty] | 1.1 | -0.3 | [6 empty] | 7.5 | [8 empty] | 0.2 | -1.2 | [6 empty] | 7.5 | [8 empty] | -1.6 | -1 | [6 empty] | 7.5 | [8 empty] | -0.9 | -1.7
|  | 15 | [8 empty] | 1.1 | -0.4 | 1.1 | -0.28672 |  |  |  |  | 15 | [8 empty] | 0.1 | -1.1 | 0.054686 | -1.032 |  |  |  |  | 15 | [8 empty] | -1.2 | -1 | -1.2 | -1.0453 |  |  |  |  | 15 | [8 empty] | -0.6 | -1.6 | -0.64531 | -1.6227 |  |  |  |  | 15 | [8 empty] | 1.1 | -0.4 | [6 empty] | 15 | [8 empty] | 0.1 | -1.1 | [6 empty] | 15 | [8 empty] | -1.2 | -1 | [6 empty] | 15 | [8 empty] | -0.6 | -1.6
|  | 22.5 | [8 empty] | 1.1 | 0.1 | [6 empty] | 22.5 | [8 empty] | -0.1 | -0.8 | [6 empty] | 22.5 | [8 empty] | -1.2 | -1.2 | [6 empty] | 22.5 | [8 empty] | -0.8 | -1.7 | [6 empty] | 22.5 | [8 empty] | 1.1 | 0.1 | [6 empty] | 22.5 | [8 empty] | -0.1 | -0.8 | [6 empty] | 22.5 | [8 empty] | -1.2 | -1.2 | [6 empty] | 22.5 | [8 empty] | -0.8 | -1.7
|  | 30 | [8 empty] | 1.3 | 0.3 | [6 empty] | 30 | [8 empty] | -0.1 | -0.9 | [6 empty] | 30 | [8 empty] | -0.7 | -0.7 | [6 empty] | 30 | [8 empty] | -0.2 | -1.1 | [6 empty] | 30 | [8 empty] | 1.3 | 0.3 | 1.3 | 0.33855 |  |  |  |  | 30 | [8 empty] | -0.1 | -0.9 | -0.11285 | -0.86145 |  |  |  |  | 30 | [8 empty] | -0.7 | -0.7 | -0.68715 | -0.68715 |  |  |  |  | 30 | [8 empty] | -0.2 | -1.1 | -0.21285 | -1.0743
|  | 37.5 | [8 empty] | 1.3 | 0.6 | [6 empty] | 37.5 | [8 empty] | -0.2 | -0.6 | [6 empty] | 37.5 | [8 empty] | -0.6 | -0.6 | [6 empty] | 37.5 | [8 empty] | -0.3 | -0.9 | [6 empty] | 37.5 | [8 empty] | 1.3 | 0.6 | [6 empty] | 37.5 | [8 empty] | -0.2 | -0.6 | [6 empty] | 37.5 | [8 empty] | -0.6 | -0.6 | [6 empty] | 37.5 | [8 empty] | -0.3 | -0.9
|  | 45 | [8 empty] | 1.1 | 0.9 | [6 empty] | 45 | [8 empty] | -0.3 | -0.5 | [6 empty] | 45 | [8 empty] | -0.5 | -0.5 | [6 empty] | 45 | [8 empty] | -0.3 | -0.7 | [6 empty] | 45 | [8 empty] | 1.1 | 0.9 | [6 empty] | 45 | [8 empty] | -0.3 | -0.5 | [6 empty] | 45 | [8 empty] | -0.5 | -0.5 | [6 empty] | 45 | [8 empty] | -0.3 | -0.7
[12 empty] | CN | 1.1 | -0.28672 | [14 empty] | CN | 0.054686 | -1.032 | [14 empty] | CN | -1.2 | -1.0453 | [14 empty] | CN | -0.64531 | -1.6227 | [14 empty] | CN | 1.3 | 0.33855 | [14 empty] | CN | -0.11285 | -0.86145 | [14 empty] | CN | -0.68715 | -0.68715 | [14 empty] | CN | -0.21285 | -1.0743
| Side surfaces | Horizontal distance from windward edge | [15 empty] | Side surfaces | Horizontal distance from windward edge | [15 empty] | Side surfaces | Horizontal distance from windward edge | [15 empty] | Side surfaces | Horizontal distance from windward edge | [13 empty] | Horizontal distance from windward edge | [15 empty] | Horizontal distance from windward edge | [15 empty] | Horizontal distance from windward edge | [15 empty] | Horizontal distance from windward edge
| h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h
| Load case A - Clear wind flow |  |  |  |  | -0.8 | -0.8 | -0.6 | -0.3 | [8 empty] | Load case A - Clear wind flow | [16 empty] | Load case A - Clear wind flow | [16 empty] | Load case A - Clear wind flow | [16 empty] | Load case A - Clear wind flow |  |  |  |  | -0.8 | -0.8 | -0.6 | -0.3 | [8 empty] | Load case A - Clear wind flow | [16 empty] | Load case A - Clear wind flow | [16 empty] | Load case A - Clear wind flow
| Load case A - Obstructed wind flow | [16 empty] | Load case A - Obstructed wind flow | [16 empty] | Load case A - Obstructed wind flow |  |  |  |  | -1.2 | -1.2 | -0.9 | -0.6 | [8 empty] | Load case A - Obstructed wind flow | [16 empty] | Load case A - Obstructed wind flow | [16 empty] | Load case A - Obstructed wind flow | [16 empty] | Load case A - Obstructed wind flow |  |  |  |  | -1.2 | -1.2 | -0.9 | -0.6 | [8 empty] | Load case A - Obstructed wind flow
| Load case B - Clear wind flow | [16 empty] | Load case B - Clear wind flow |  |  |  |  | 0.8 | 0.8 | 0.5 | 0.3 | [8 empty] | Load case B - Clear wind flow | [16 empty] | Load case B - Clear wind flow | [16 empty] | Load case B - Clear wind flow | [16 empty] | Load case B - Clear wind flow |  |  |  |  | 0.8 | 0.8 | 0.5 | 0.3 | [8 empty] | Load case B - Clear wind flow | [16 empty] | Load case B - Clear wind flow
| Load case B - Obstructed wind flow | [16 empty] | Load case B - Obstructed wind flow | [16 empty] | Load case B - Obstructed wind flow | [16 empty] | Load case B - Obstructed wind flow |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.3 | [8 empty] | Load case B - Obstructed wind flow | [16 empty] | Load case B - Obstructed wind flow | [16 empty] | Load case B - Obstructed wind flow | [16 empty] | Load case B - Obstructed wind flow |  |  |  |  | 0.5 | 0.5 | 0.5 | 0.3
[5 empty] | CN | -0.8 | -0.8 | -0.6 | -0.3 | [12 empty] | CN | 0.8 | 0.8 | 0.5 | 0.3 | [12 empty] | CN | -1.2 | -1.2 | -0.9 | -0.6 | [12 empty] | CN | 0.5 | 0.5 | 0.5 | 0.3 | [12 empty] | CN | -0.8 | -0.8 | -0.6 | -0.3 | [12 empty] | CN | 0.8 | 0.8 | 0.5 | 0.3 | [12 empty] | CN | -1.2 | -1.2 | -0.9 | -0.6 | [12 empty] | CN | 0.5 | 0.5 | 0.5 | 0.3
6.2 - Cp FOR PARTIALLY ENCLOSED & ENCLOSED | [16 empty] | 6.2 - Cp FOR PARTIALLY ENCLOSED & ENCLOSED | [16 empty] | 6.2 - Cp FOR PARTIALLY ENCLOSED & ENCLOSED | [16 empty] | 6.2 - Cp FOR PARTIALLY ENCLOSED & ENCLOSED | [16 empty] | 6.2 - Cp FOR PARTIALLY ENCLOSED & ENCLOSED | [16 empty] | 6.2 - Cp FOR PARTIALLY ENCLOSED & ENCLOSED | [16 empty] | 6.2 - Cp FOR PARTIALLY ENCLOSED & ENCLOSED | [16 empty] | 6.2 - Cp FOR PARTIALLY ENCLOSED & ENCLOSED
Step 6.2: Determine external pressure coefficient, Cp, for partially enclosed & enclosed buildings | [16 empty] | Step 6.2: Determine external pressure coefficient, Cp, for partially enclosed & enclosed buildings | [16 empty] | Step 6.2: Determine external pressure coefficient, Cp, for partially enclosed & enclosed buildings | [16 empty] | Step 6.2: Determine external pressure coefficient, Cp, for partially enclosed & enclosed buildings | [16 empty] | Step 6.2: Determine external pressure coefficient, Cp, for partially enclosed & enclosed buildings | [16 empty] | Step 6.2: Determine external pressure coefficient, Cp, for partially enclosed & enclosed buildings | [16 empty] | Step 6.2: Determine external pressure coefficient, Cp, for partially enclosed & enclosed buildings | [16 empty] | Step 6.2: Determine external pressure coefficient, Cp, for partially enclosed & enclosed buildings
| Fig. 27.4-1 for walls and gable or hip roofs | [16 empty] | Fig. 27.4-1 for walls and gable or hip roofs | [16 empty] | Fig. 27.4-1 for walls and gable or hip roofs | [16 empty] | Fig. 27.4-1 for walls and gable or hip roofs | [16 empty] | Fig. 27.4-1 for walls and gable or hip roofs | [16 empty] | Fig. 27.4-1 for walls and gable or hip roofs | [16 empty] | Fig. 27.4-1 for walls and gable or hip roofs | [16 empty] | Fig. 27.4-1 for walls and gable or hip roofs
| Since the wind direction is | X | [15 empty] | Since the wind direction is | X | [15 empty] | Since the wind direction is | X | [15 empty] | Since the wind direction is | X | [15 empty] | Since the wind direction is | Y | [15 empty] | Since the wind direction is | Y | [15 empty] | Since the wind direction is | Y | [15 empty] | Since the wind direction is | Y
| the non-zero ridge is | parallel | to the non-zero ridge | [14 empty] | the non-zero ridge is | parallel | to the non-zero ridge | [14 empty] | the non-zero ridge is | parallel | to the non-zero ridge | [14 empty] | the non-zero ridge is | parallel | to the non-zero ridge | [14 empty] | the non-zero ridge is | normal | to the non-zero ridge | [14 empty] | the non-zero ridge is | normal | to the non-zero ridge | [14 empty] | the non-zero ridge is | normal | to the non-zero ridge | [14 empty] | the non-zero ridge is | normal | to the non-zero ridge
| The windward and leeward roof surfaces are | +X & -X | [15 empty] | The windward and leeward roof surfaces are | +X & -X | [15 empty] | The windward and leeward roof surfaces are | +X & -X | [15 empty] | The windward and leeward roof surfaces are | +X & -X | [15 empty] | The windward and leeward roof surfaces are | +Y & -Y | [15 empty] | The windward and leeward roof surfaces are | +Y & -Y | [15 empty] | The windward and leeward roof surfaces are | +Y & -Y | [15 empty] | The windward and leeward roof surfaces are | +Y & -Y
| and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638
| The side rood surfaces are | +Y & -Y | [15 empty] | The side rood surfaces are | +Y & -Y | [15 empty] | The side rood surfaces are | +Y & -Y | [15 empty] | The side rood surfaces are | +Y & -Y | [15 empty] | The side rood surfaces are | +X & -X | [15 empty] | The side rood surfaces are | +X & -X | [15 empty] | The side rood surfaces are | +X & -X | [15 empty] | The side rood surfaces are | +X & -X
| and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 30.9638 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993 | [15 empty] | and the corresponding roof pitch angle is | 16.6993
| Tent dimension normal to wind direction (B) | 20 | [15 empty] | Tent dimension normal to wind direction (B) | 20 | [15 empty] | Tent dimension normal to wind direction (B) | 20 | [15 empty] | Tent dimension normal to wind direction (B) | 20 | [15 empty] | Tent dimension normal to wind direction (B) | 40 | [15 empty] | Tent dimension normal to wind direction (B) | 40 | [15 empty] | Tent dimension normal to wind direction (B) | 40 | [15 empty] | Tent dimension normal to wind direction (B) | 40
| Tent dimension parallel to wind direction (L) | 40 | [15 empty] | Tent dimension parallel to wind direction (L) | 40 | [15 empty] | Tent dimension parallel to wind direction (L) | 40 | [15 empty] | Tent dimension parallel to wind direction (L) | 40 | [15 empty] | Tent dimension parallel to wind direction (L) | 20 | [15 empty] | Tent dimension parallel to wind direction (L) | 20 | [15 empty] | Tent dimension parallel to wind direction (L) | 20 | [15 empty] | Tent dimension parallel to wind direction (L) | 20
| Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11
| Load case (A or B) | A | [15 empty] | Load case (A or B) | B | [15 empty] | Load case (A or B) | A | [15 empty] | Load case (A or B) | B | [15 empty] | Load case (A or B) | A | [15 empty] | Load case (A or B) | B | [15 empty] | Load case (A or B) | A | [15 empty] | Load case (A or B) | B
| Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. | [16 empty] | Plus and minus signs signify pressures acting toward and away from the surfaces, respectively.
| For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively. | [16 empty] | For GCpi, plus and minus signs signify pressures acting toward and away from the internal surfaces, respectively.
| B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction. | [16 empty] | B: Horizontal dimension of building measured normal to wind direction.
| L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction. | [16 empty] | L: Horizontal dimension of building measured parallel to wind direction.
| h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees | [16 empty] | h: Mean roof height, except that eave height shall be used for θ ≤ 10 degrees
| Windward roof | [16 empty] | Windward roof | [16 empty] | Windward roof | [16 empty] | Windward roof | [16 empty] | Windward roof | [16 empty] | Windward roof | [16 empty] | Windward roof | [16 empty] | Windward roof
| Wind direction normal to ridge & Windward: | [16 empty] | Wind direction normal to ridge & Windward: | [16 empty] | Wind direction normal to ridge & Windward: | [16 empty] | Wind direction normal to ridge & Windward: | [16 empty] | Wind direction normal to ridge & Windward: | [16 empty] | Wind direction normal to ridge & Windward: | [16 empty] | Wind direction normal to ridge & Windward: | [16 empty] | Wind direction normal to ridge & Windward:
| Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.55 | [15 empty] | Ratio h/L_inter | 0.55 | [15 empty] | Ratio h/L_inter | 0.55 | [15 empty] | Ratio h/L_inter | 0.55
| h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 16.6993 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 16.6993 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 16.6993 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 16.6993 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 30.9638 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 30.9638 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 30.9638 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 30.9638
| 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25
| 0.25 | -0.7 | -0.5 | -0.3 | -0.2 | -0.2 | 0 | 0.4 | 0.6 | [8 empty] | 0.25 | -0.18 | 0 | 0.2 | 0.3 | 0.3 | 0.4 | 0.4 | 0.6 | [8 empty] | 0.25 | -0.7 | -0.5 | -0.3 | -0.2 | -0.2 | 0 | 0.4 | 0.6 | [8 empty] | 0.25 | -0.18 | 0 | 0.2 | 0.3 | 0.3 | 0.4 | 0.4 | 0.6 | [8 empty] | 0.25 | -0.7 | -0.5 | -0.3 | -0.2 | -0.2 | 0 | 0.4 | 0.6 | [8 empty] | 0.25 | -0.18 | 0 | 0.2 | 0.3 | 0.3 | 0.4 | 0.4 | 0.6 | [8 empty] | 0.25 | -0.7 | -0.5 | -0.3 | -0.2 | -0.2 | 0 | 0.4 | 0.6 | [8 empty] | 0.25 | -0.18 | 0 | 0.2 | 0.3 | 0.3 | 0.4 | 0.4 | 0.6
| 0.25-0.5 | -0.72 | -0.52 | -0.31 | -0.21 | -0.2 | -0.02 | 0.36 | 0.6 | -0.44863 | [7 empty] | 0.25-0.5 | -0.18 | -0.018 | 0.18 | 0.29 | 0.29 | 0.39 | 0.4 | 0.6 | 0.049291 | [7 empty] | 0.25-0.5 | -0.72 | -0.52 | -0.31 | -0.21 | -0.2 | -0.02 | 0.36 | 0.6 | -0.44863 | [7 empty] | 0.25-0.5 | -0.18 | -0.018 | 0.18 | 0.29 | 0.29 | 0.39 | 0.4 | 0.6 | 0.049291 | [7 empty] | 0.25-0.5 | [16 empty] | 0.25-0.5 | [16 empty] | 0.25-0.5 | [16 empty] | 0.25-0.5
| 0.5 | -0.9 | -0.7 | -0.4 | -0.3 | -0.2 | -0.2 | 0 | 0.6 | [8 empty] | 0.5 | -0.18 | -0.18 | 0 | 0.2 | 0.2 | 0.3 | 0.4 | 0.6 | [8 empty] | 0.5 | -0.9 | -0.7 | -0.4 | -0.3 | -0.2 | -0.2 | 0 | 0.6 | [8 empty] | 0.5 | -0.18 | -0.18 | 0 | 0.2 | 0.2 | 0.3 | 0.4 | 0.6 | [8 empty] | 0.5 | -0.9 | -0.7 | -0.4 | -0.3 | -0.2 | -0.2 | 0 | 0.6 | [8 empty] | 0.5 | -0.18 | -0.18 | 0 | 0.2 | 0.2 | 0.3 | 0.4 | 0.6 | [8 empty] | 0.5 | -0.9 | -0.7 | -0.4 | -0.3 | -0.2 | -0.2 | 0 | 0.6 | [8 empty] | 0.5 | -0.18 | -0.18 | 0 | 0.2 | 0.2 | 0.3 | 0.4 | 0.6
| 0.5-1.0 | [16 empty] | 0.5-1.0 | [16 empty] | 0.5-1.0 | [16 empty] | 0.5-1.0 | [16 empty] | 0.5-1.0 | -0.94 | -0.73 | -0.43 | -0.32 | -0.21 | -0.2 | 0 | 0.6 | -0.20807 | [7 empty] | 0.5-1.0 | -0.18 | -0.18 | -0.018 | 0.18 | 0.2 | 0.29 | 0.39 | 0.6 | 0.21735 | [7 empty] | 0.5-1.0 | -0.94 | -0.73 | -0.43 | -0.32 | -0.21 | -0.2 | 0 | 0.6 | -0.20807 | [7 empty] | 0.5-1.0 | -0.18 | -0.18 | -0.018 | 0.18 | 0.2 | 0.29 | 0.39 | 0.6 | 0.21735
| 1 | -1.3 | -1 | -0.7 | -0.5 | -0.3 | -0.2 | 0 | 0.6 | [8 empty] | 1 | -0.18 | -0.18 | -0.18 | 0 | 0.2 | 0.2 | 0.3 | 0.6 | [8 empty] | 1 | -1.3 | -1 | -0.7 | -0.5 | -0.3 | -0.2 | 0 | 0.6 | [8 empty] | 1 | -0.18 | -0.18 | -0.18 | 0 | 0.2 | 0.2 | 0.3 | 0.6 | [8 empty] | 1 | -1.3 | -1 | -0.7 | -0.5 | -0.3 | -0.2 | 0 | 0.6 | [8 empty] | 1 | -0.18 | -0.18 | -0.18 | 0 | 0.2 | 0.2 | 0.3 | 0.6 | [8 empty] | 1 | -1.3 | -1 | -0.7 | -0.5 | -0.3 | -0.2 | 0 | 0.6 | [8 empty] | 1 | -0.18 | -0.18 | -0.18 | 0 | 0.2 | 0.2 | 0.3 | 0.6
| >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0
[9 empty] | Cp | -0.44863 | [15 empty] | Cp | 0.049291 | [15 empty] | Cp | -0.44863 | [15 empty] | Cp | 0.049291 | [15 empty] | Cp | -0.20807 | [15 empty] | Cp | 0.21735 | [15 empty] | Cp | -0.20807 | [15 empty] | Cp | 0.21735
| Leeward roof | [16 empty] | Leeward roof | [16 empty] | Leeward roof | [16 empty] | Leeward roof | [16 empty] | Leeward roof | [16 empty] | Leeward roof | [16 empty] | Leeward roof | [16 empty] | Leeward roof
| Wind direction normal to ridge & Leeward: | [16 empty] | Wind direction normal to ridge & Leeward: | [16 empty] | Wind direction normal to ridge & Leeward: | [16 empty] | Wind direction normal to ridge & Leeward: | [16 empty] | Wind direction normal to ridge & Leeward: | [16 empty] | Wind direction normal to ridge & Leeward: | [16 empty] | Wind direction normal to ridge & Leeward: | [16 empty] | Wind direction normal to ridge & Leeward:
| Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.55 | [15 empty] | Ratio h/L_inter | 0.55 | [15 empty] | Ratio h/L_inter | 0.55 | [15 empty] | Ratio h/L_inter | 0.55
| h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 16.6993 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 16.6993 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 16.6993 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 16.6993 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 30.9638 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 30.9638 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 30.9638 | [7 empty] | h/L_inter ¦ theta | 10 | 15 | 20 | 25 | 30 | 35 | 45 | 60 | 30.9638
| 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25 | [16 empty] | 0-0.25
| 0.25 | -0.3 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.25 | -0.3 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.25 | -0.3 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.25 | -0.3 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.25 | -0.3 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.25 | -0.3 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.25 | -0.3 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.25 | -0.3 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6
| 0.25-0.5 | -0.32 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.53399 | [7 empty] | 0.25-0.5 | -0.32 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.53399 | [7 empty] | 0.25-0.5 | -0.32 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.53399 | [7 empty] | 0.25-0.5 | -0.32 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.53399 | [7 empty] | 0.25-0.5 | [16 empty] | 0.25-0.5 | [16 empty] | 0.25-0.5 | [16 empty] | 0.25-0.5
| 0.5 | -0.5 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.5 | -0.5 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.5 | -0.5 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.5 | -0.5 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.5 | -0.5 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.5 | -0.5 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.5 | -0.5 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 0.5 | -0.5 | -0.5 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6
| 0.5-1.0 | [16 empty] | 0.5-1.0 | [16 empty] | 0.5-1.0 | [16 empty] | 0.5-1.0 | [16 empty] | 0.5-1.0 | -0.52 | -0.51 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [7 empty] | 0.5-1.0 | -0.52 | -0.51 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [7 empty] | 0.5-1.0 | -0.52 | -0.51 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [7 empty] | 0.5-1.0 | -0.52 | -0.51 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6
| 1 | -0.7 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 1 | -0.7 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 1 | -0.7 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 1 | -0.7 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 1 | -0.7 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 1 | -0.7 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 1 | -0.7 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | [8 empty] | 1 | -0.7 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6 | -0.6
| >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0 | [16 empty] | >1.0
[9 empty] | Cp | -0.53399 | [15 empty] | Cp | -0.53399 | [15 empty] | Cp | -0.53399 | [15 empty] | Cp | -0.53399 | [15 empty] | Cp | -0.6 | [15 empty] | Cp | -0.6 | [15 empty] | Cp | -0.6 | [15 empty] | Cp | -0.6
| Roof side surfaces | [16 empty] | Roof side surfaces | [16 empty] | Roof side surfaces | [16 empty] | Roof side surfaces | [16 empty] | Roof side surfaces | [16 empty] | Roof side surfaces | [16 empty] | Roof side surfaces | [16 empty] | Roof side surfaces
| Wind direction parallel to ridge (Sides) | [16 empty] | Wind direction parallel to ridge (Sides) | [16 empty] | Wind direction parallel to ridge (Sides) | [16 empty] | Wind direction parallel to ridge (Sides) | [16 empty] | Wind direction parallel to ridge (Sides) | [16 empty] | Wind direction parallel to ridge (Sides) | [16 empty] | Wind direction parallel to ridge (Sides) | [16 empty] | Wind direction parallel to ridge (Sides)
| Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.275 | [15 empty] | Ratio h/L_inter | 0.55 | [15 empty] | Ratio h/L_inter | 0.55 | [15 empty] | Ratio h/L_inter | 0.55 | [15 empty] | Ratio h/L_inter | 0.55
|  | Horizontal distance from windward edge | [16 empty] | Horizontal distance from windward edge | [16 empty] | Horizontal distance from windward edge | [16 empty] | Horizontal distance from windward edge | [13 empty] | Horizontal distance from windward edge | [15 empty] | Horizontal distance from windward edge | [15 empty] | Horizontal distance from windward edge | [15 empty] | Horizontal distance from windward edge
| h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [8 empty] | h/L_inter | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h
| 0-0.5 | -0.9 | -0.9 | -0.5 | -0.3 | -0.9 | -0.9 | -0.5 | -0.3 | [8 empty] | 0-0.5 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | [8 empty] | 0-0.5 | -0.9 | -0.9 | -0.5 | -0.3 | -0.9 | -0.9 | -0.5 | -0.3 | [8 empty] | 0-0.5 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | [8 empty] | 0-0.5 | -0.9 | -0.9 | -0.5 | -0.3 | [12 empty] | 0-0.5 | -0.18 | -0.18 | -0.18 | -0.18 | [12 empty] | 0-0.5 | -0.9 | -0.9 | -0.5 | -0.3 | [12 empty] | 0-0.5 | -0.18 | -0.18 | -0.18 | -0.18
| 0.5-1.0 | [16 empty] | 0.5-1.0 | [16 empty] | 0.5-1.0 | [16 empty] | 0.5-1.0 | [16 empty] | 0.5-1.0 | -0.94 | -0.88 | -0.52 | -0.34 | -0.94 | -0.88 | -0.52 | -0.34 | [8 empty] | 0.5-1.0 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | [8 empty] | 0.5-1.0 | -0.94 | -0.88 | -0.52 | -0.34 | -0.94 | -0.88 | -0.52 | -0.34 | [8 empty] | 0.5-1.0 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18 | -0.18
| >=1.0 | -1.3 | -0.7 | -0.7 | -0.7 | [12 empty] | >=1.0 | -0.18 | -0.18 | -0.18 | -0.18 | [12 empty] | >=1.0 | -1.3 | -0.7 | -0.7 | -0.7 | [12 empty] | >=1.0 | -0.18 | -0.18 | -0.18 | -0.18 | [12 empty] | >=1.0 | -1.3 | -0.7 | -0.7 | -0.7 | [12 empty] | >=1.0 | -0.18 | -0.18 | -0.18 | -0.18 | [12 empty] | >=1.0 | -1.3 | -0.7 | -0.7 | -0.7 | [12 empty] | >=1.0 | -0.18 | -0.18 | -0.18 | -0.18
| h | 11 |  |  | From windward edge to | 5.5 | 11 | 22 | 40 | [8 empty] | h | 11 |  |  | From windward edge to | 5.5 | 11 | 22 | 40 | [8 empty] | h | 11 |  |  | From windward edge to | 5.5 | 11 | 22 | 40 | [8 empty] | h | 11 |  |  | From windward edge to | 5.5 | 11 | 22 | 40 | [8 empty] | h | 11 |  |  | From windward edge to | 5.5 | 11 | 20 | [9 empty] | h | 11 |  |  | From windward edge to | 5.5 | 11 | 20 | [9 empty] | h | 11 |  |  | From windward edge to | 5.5 | 11 | 20 | [9 empty] | h | 11 |  |  | From windward edge to | 5.5 | 11 | 20
| L | 40 |  |  | Cp | -0.9 | -0.9 | -0.5 | -0.3 | [8 empty] | L | 40 |  |  | Cp | -0.18 | -0.18 | -0.18 | -0.18 | [8 empty] | L | 40 |  |  | Cp | -0.9 | -0.9 | -0.5 | -0.3 | [8 empty] | L | 40 |  |  | Cp | -0.18 | -0.18 | -0.18 | -0.18 | [8 empty] | L | 20 |  |  | Cp | -0.94 | -0.88 | -0.52 | -0.34 | [8 empty] | L | 20 |  |  | Cp | -0.18 | -0.18 | -0.18 | -0.18 | [8 empty] | L | 20 |  |  | Cp | -0.94 | -0.88 | -0.52 | -0.34 | [8 empty] | L | 20 |  |  | Cp | -0.18 | -0.18 | -0.18 | -0.18
| Windward wall | Cp | 0.8 | [14 empty] | Windward wall | Cp | 0.8 | [14 empty] | Windward wall | Cp | 0.8 | [14 empty] | Windward wall | Cp | 0.8 | [14 empty] | Windward wall | Cp | 0.8 | [14 empty] | Windward wall | Cp | 0.8 | [14 empty] | Windward wall | Cp | 0.8 | [14 empty] | Windward wall | Cp | 0.8
| Leeward wall | L/B | 2 | 0-1 | 1-2 | 2 | 2-4 | >4 | [9 empty] | Leeward wall | L/B | 2 | 0-1 | 1-2 | 2 | 2-4 | >4 | [9 empty] | Leeward wall | L/B | 2 | 0-1 | 1-2 | 2 | 2-4 | >4 | [9 empty] | Leeward wall | L/B | 2 | 0-1 | 1-2 | 2 | 2-4 | >4 | [9 empty] | Leeward wall | L/B | 0.5 | 0-1 | 1-2 | 2 | 2-4 | >4 | [9 empty] | Leeward wall | L/B | 0.5 | 0-1 | 1-2 | 2 | 2-4 | >4 | [9 empty] | Leeward wall | L/B | 0.5 | 0-1 | 1-2 | 2 | 2-4 | >4 | [9 empty] | Leeward wall | L/B | 0.5 | 0-1 | 1-2 | 2 | 2-4 | >4
|  |  |  | -0.5 | interp | -0.3 | interp | -0.2 | [12 empty] | -0.5 | interp | -0.3 | interp | -0.2 | [12 empty] | -0.5 | interp | -0.3 | interp | -0.2 | [12 empty] | -0.5 | interp | -0.3 | interp | -0.2 | [12 empty] | -0.5 | interp | -0.3 | interp | -0.2 | [12 empty] | -0.5 | interp | -0.3 | interp | -0.2 | [12 empty] | -0.5 | interp | -0.3 | interp | -0.2 | [12 empty] | -0.5 | interp | -0.3 | interp | -0.2
|  | Cp | -0.3 |  |  | -0.3 | [12 empty] | Cp | -0.3 |  |  | -0.3 | [12 empty] | Cp | -0.3 |  |  | -0.3 | [12 empty] | Cp | -0.3 |  |  | -0.3 | [12 empty] | Cp | -0.5 | -0.5 | [14 empty] | Cp | -0.5 | -0.5 | [14 empty] | Cp | -0.5 | -0.5 | [14 empty] | Cp | -0.5 | -0.5
| Side walls | Cp | -0.7 | [14 empty] | Side walls | Cp | -0.7 | [14 empty] | Side walls | Cp | -0.7 | [14 empty] | Side walls | Cp | -0.7 | [14 empty] | Side walls | Cp | -0.7 | [14 empty] | Side walls | Cp | -0.7 | [14 empty] | Side walls | Cp | -0.7 | [14 empty] | Side walls | Cp | -0.7
7.1 - p FOR OPEN | [16 empty] | 7.1 - p FOR OPEN | [16 empty] | 7.1 - p FOR OPEN | [16 empty] | 7.1 - p FOR OPEN | [16 empty] | 7.1 - p FOR OPEN | [16 empty] | 7.1 - p FOR OPEN | [16 empty] | 7.1 - p FOR OPEN | [16 empty] | 7.1 - p FOR OPEN
Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface
| Open | [16 empty] | Open | [16 empty] | Open | [16 empty] | Open | [16 empty] | Open | [16 empty] | Open | [16 empty] | Open | [16 empty] | Open
| Eq. 27.4-3 for open buildings | [16 empty] | Eq. 27.4-3 for open buildings | [16 empty] | Eq. 27.4-3 for open buildings | [16 empty] | Eq. 27.4-3 for open buildings | [16 empty] | Eq. 27.4-3 for open buildings | [16 empty] | Eq. 27.4-3 for open buildings | [16 empty] | Eq. 27.4-3 for open buildings | [16 empty] | Eq. 27.4-3 for open buildings
| p = qh*G*CN | [16 empty] | p = qh*G*CN | [16 empty] | p = qh*G*CN | [16 empty] | p = qh*G*CN | [16 empty] | p = qh*G*CN | [16 empty] | p = qh*G*CN | [16 empty] | p = qh*G*CN | [16 empty] | p = qh*G*CN
| GCpi is not used in Open | [16 empty] | GCpi is not used in Open | [16 empty] | GCpi is not used in Open | [16 empty] | GCpi is not used in Open | [16 empty] | GCpi is not used in Open | [16 empty] | GCpi is not used in Open | [16 empty] | GCpi is not used in Open | [16 empty] | GCpi is not used in Open
| Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y
| Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y
| Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X
| Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X
| Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y
| Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y
| Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X
| Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X
| Open / Partially Enclosed / Enclosed | Open | [15 empty] | Open / Partially Enclosed / Enclosed | Open | [15 empty] | Open / Partially Enclosed / Enclosed | Open | [15 empty] | Open / Partially Enclosed / Enclosed | Open | [15 empty] | Open / Partially Enclosed / Enclosed | Open | [15 empty] | Open / Partially Enclosed / Enclosed | Open | [15 empty] | Open / Partially Enclosed / Enclosed | Open | [15 empty] | Open / Partially Enclosed / Enclosed | Open
[9 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge
[9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h
|  |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2
|  |  | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X
|  | p (psf) | 0 | 0 | 0 | 0 | 0.98638 | -0.2571 | -0.71737 | -0.71737 | -0.53803 | -0.26901 | -0.71737 | -0.71737 | -0.53803 | -0.26901 |  |  | p (psf) | 0 | 0 | 0 | 0 | 0.049038 | -0.92543 | 0.71737 | 0.71737 | 0.44836 | 0.26901 | 0.71737 | 0.71737 | 0.44836 | 0.26901 |  |  | p (psf) | 0 | 0 | 0 | 0 | -1.0761 | -0.93735 | -1.0761 | -1.0761 | -0.80704 | -0.53803 | -1.0761 | -1.0761 | -0.80704 | -0.53803 |  |  | p (psf) | 0 | 0 | 0 | 0 | -0.57866 | -1.4551 | 0.44836 | 0.44836 | 0.44836 | 0.26901 | 0.44836 | 0.44836 | 0.44836 | 0.26901 |  |  | p (psf) | 0 | 0 | 0 | 0 | 1.1657 | 0.30358 | -0.71737 | -0.71737 | -0.53803 | -0.26901 | -0.71737 | -0.71737 | -0.53803 | -0.26901 |  |  | p (psf) | 0 | 0 | 0 | 0 | -0.10119 | -0.77247 | 0.71737 | 0.71737 | 0.44836 | 0.26901 | 0.71737 | 0.71737 | 0.44836 | 0.26901 |  |  | p (psf) | 0 | 0 | 0 | 0 | -0.61618 | -0.61618 | -1.0761 | -1.0761 | -0.80704 | -0.53803 | -1.0761 | -1.0761 | -0.80704 | -0.53803 |  |  | p (psf) | 0 | 0 | 0 | 0 | -0.19087 | -0.96334 | 0.44836 | 0.44836 | 0.44836 | 0.26901 | 0.44836 | 0.44836 | 0.44836 | 0.26901
7.2 - p FOR PARTIALLY ENCLOSED | [16 empty] | 7.2 - p FOR PARTIALLY ENCLOSED | [16 empty] | 7.2 - p FOR PARTIALLY ENCLOSED | [16 empty] | 7.2 - p FOR PARTIALLY ENCLOSED | [16 empty] | 7.2 - p FOR PARTIALLY ENCLOSED | [16 empty] | 7.2 - p FOR PARTIALLY ENCLOSED | [16 empty] | 7.2 - p FOR PARTIALLY ENCLOSED | [16 empty] | 7.2 - p FOR PARTIALLY ENCLOSED
Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface | [16 empty] | Step 7: Calculate wind pressure, p, on each building surface
| Partially enclosed | [16 empty] | Partially enclosed | [16 empty] | Partially enclosed | [16 empty] | Partially enclosed | [16 empty] | Partially enclosed | [16 empty] | Partially enclosed | [16 empty] | Partially enclosed | [16 empty] | Partially enclosed
| Eq. 27.4-1 for rigid buildings |  |  |  | Note: | [12 empty] | Eq. 27.4-1 for rigid buildings |  |  |  | Note: | [12 empty] | Eq. 27.4-1 for rigid buildings |  |  |  | Note: | [12 empty] | Eq. 27.4-1 for rigid buildings |  |  |  | Note: | [12 empty] | Eq. 27.4-1 for rigid buildings |  |  |  | Note: | [12 empty] | Eq. 27.4-1 for rigid buildings |  |  |  | Note: | [12 empty] | Eq. 27.4-1 for rigid buildings |  |  |  | Note: | [12 empty] | Eq. 27.4-1 for rigid buildings |  |  |  | Note:
| Eq. 27.4-2 for flexible buildings |  |  |  | qi = qh for windward walls, side walls, leeward walls, and | [12 empty] | Eq. 27.4-2 for flexible buildings |  |  |  | qi = qh for windward walls, side walls, leeward walls, and | [12 empty] | Eq. 27.4-2 for flexible buildings |  |  |  | qi = qh for windward walls, side walls, leeward walls, and | [12 empty] | Eq. 27.4-2 for flexible buildings |  |  |  | qi = qh for windward walls, side walls, leeward walls, and | [12 empty] | Eq. 27.4-2 for flexible buildings |  |  |  | qi = qh for windward walls, side walls, leeward walls, and | [12 empty] | Eq. 27.4-2 for flexible buildings |  |  |  | qi = qh for windward walls, side walls, leeward walls, and | [12 empty] | Eq. 27.4-2 for flexible buildings |  |  |  | qi = qh for windward walls, side walls, leeward walls, and | [12 empty] | Eq. 27.4-2 for flexible buildings |  |  |  | qi = qh for windward walls, side walls, leeward walls, and
| p = q*G*Cp – qi*(GCpi) |  |  |  | roofs of enclosed buildings and for negative internal | [12 empty] | p = q*G*Cp – qi*(GCpi) |  |  |  | roofs of enclosed buildings and for negative internal | [12 empty] | p = q*G*Cp – qi*(GCpi) |  |  |  | roofs of enclosed buildings and for negative internal | [12 empty] | p = q*G*Cp – qi*(GCpi) |  |  |  | roofs of enclosed buildings and for negative internal | [12 empty] | p = q*G*Cp – qi*(GCpi) |  |  |  | roofs of enclosed buildings and for negative internal | [12 empty] | p = q*G*Cp – qi*(GCpi) |  |  |  | roofs of enclosed buildings and for negative internal | [12 empty] | p = q*G*Cp – qi*(GCpi) |  |  |  | roofs of enclosed buildings and for negative internal | [12 empty] | p = q*G*Cp – qi*(GCpi) |  |  |  | roofs of enclosed buildings and for negative internal
[5 empty] | pressure evaluation in partially enclosed buildings | [16 empty] | pressure evaluation in partially enclosed buildings | [16 empty] | pressure evaluation in partially enclosed buildings | [16 empty] | pressure evaluation in partially enclosed buildings | [16 empty] | pressure evaluation in partially enclosed buildings | [16 empty] | pressure evaluation in partially enclosed buildings | [16 empty] | pressure evaluation in partially enclosed buildings | [16 empty] | pressure evaluation in partially enclosed buildings
| Winward wall | +X |  |  | qi = qz for positive internal pressure evaluation in partially | [12 empty] | Winward wall | +X |  |  | qi = qz for positive internal pressure evaluation in partially | [12 empty] | Winward wall | +X |  |  | qi = qz for positive internal pressure evaluation in partially | [12 empty] | Winward wall | +X |  |  | qi = qz for positive internal pressure evaluation in partially | [12 empty] | Winward wall | +Y |  |  | qi = qz for positive internal pressure evaluation in partially | [12 empty] | Winward wall | +Y |  |  | qi = qz for positive internal pressure evaluation in partially | [12 empty] | Winward wall | +Y |  |  | qi = qz for positive internal pressure evaluation in partially | [12 empty] | Winward wall | +Y |  |  | qi = qz for positive internal pressure evaluation in partially
| Leeward wall | -X |  |  | enclosed buildings where height z is defined as the level | [12 empty] | Leeward wall | -X |  |  | enclosed buildings where height z is defined as the level | [12 empty] | Leeward wall | -X |  |  | enclosed buildings where height z is defined as the level | [12 empty] | Leeward wall | -X |  |  | enclosed buildings where height z is defined as the level | [12 empty] | Leeward wall | -Y |  |  | enclosed buildings where height z is defined as the level | [12 empty] | Leeward wall | -Y |  |  | enclosed buildings where height z is defined as the level | [12 empty] | Leeward wall | -Y |  |  | enclosed buildings where height z is defined as the level | [12 empty] | Leeward wall | -Y |  |  | enclosed buildings where height z is defined as the level
| Side Wall 1 | +Y |  |  | of the highest opening in the building that could affect | [12 empty] | Side Wall 1 | +Y |  |  | of the highest opening in the building that could affect | [12 empty] | Side Wall 1 | +Y |  |  | of the highest opening in the building that could affect | [12 empty] | Side Wall 1 | +Y |  |  | of the highest opening in the building that could affect | [12 empty] | Side Wall 1 | +X |  |  | of the highest opening in the building that could affect | [12 empty] | Side Wall 1 | +X |  |  | of the highest opening in the building that could affect | [12 empty] | Side Wall 1 | +X |  |  | of the highest opening in the building that could affect | [12 empty] | Side Wall 1 | +X |  |  | of the highest opening in the building that could affect
| Side Wall 2 | -Y |  |  | the positive internal pressure. | [12 empty] | Side Wall 2 | -Y |  |  | the positive internal pressure. | [12 empty] | Side Wall 2 | -Y |  |  | the positive internal pressure. | [12 empty] | Side Wall 2 | -Y |  |  | the positive internal pressure. | [12 empty] | Side Wall 2 | -X |  |  | the positive internal pressure. | [12 empty] | Side Wall 2 | -X |  |  | the positive internal pressure. | [12 empty] | Side Wall 2 | -X |  |  | the positive internal pressure. | [12 empty] | Side Wall 2 | -X |  |  | the positive internal pressure.
| Winward roof | +X |  |  | However, since H < 15 ft, qz = qh. So no distinction. | [12 empty] | Winward roof | +X |  |  | However, since H < 15 ft, qz = qh. So no distinction. | [12 empty] | Winward roof | +X |  |  | However, since H < 15 ft, qz = qh. So no distinction. | [12 empty] | Winward roof | +X |  |  | However, since H < 15 ft, qz = qh. So no distinction. | [12 empty] | Winward roof | +Y |  |  | However, since H < 15 ft, qz = qh. So no distinction. | [12 empty] | Winward roof | +Y |  |  | However, since H < 15 ft, qz = qh. So no distinction. | [12 empty] | Winward roof | +Y |  |  | However, since H < 15 ft, qz = qh. So no distinction. | [12 empty] | Winward roof | +Y |  |  | However, since H < 15 ft, qz = qh. So no distinction.
| Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y
| Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X
| Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X
| Open / Partially Enclosed / Enclosed | Partially enclosed | [15 empty] | Open / Partially Enclosed / Enclosed | Partially enclosed | [15 empty] | Open / Partially Enclosed / Enclosed | Partially enclosed | [15 empty] | Open / Partially Enclosed / Enclosed | Partially enclosed | [15 empty] | Open / Partially Enclosed / Enclosed | Partially enclosed | [15 empty] | Open / Partially Enclosed / Enclosed | Partially enclosed | [15 empty] | Open / Partially Enclosed / Enclosed | Partially enclosed | [15 empty] | Open / Partially Enclosed / Enclosed | Partially enclosed
[9 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge
[9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h
|  |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2
|  |  | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X
|  | p (psf) | 0.13714 | -0.84924 | -1.2079 | -1.2079 | -0.98252 | -1.0591 | -1.3873 | -1.3873 | -1.0286 | -0.84924 | -1.3873 | -1.3873 | -1.0286 | -0.84924 |  |  | p (psf) | 0.13714 | -0.84924 | -1.2079 | -1.2079 | -0.53603 | -1.0591 | -0.74163 | -0.74163 | -0.74163 | -0.74163 | -0.74163 | -0.74163 | -0.74163 | -0.74163 |  |  | p (psf) | 1.2976 | 0.31121 | -0.047473 | -0.047473 | 0.17793 | 0.10139 | -0.22682 | -0.22682 | 0.13187 | 0.31121 | -0.22682 | -0.22682 | 0.13187 | 0.31121 |  |  | p (psf) | 1.2976 | 0.31121 | -0.047473 | -0.047473 | 0.62442 | 0.10139 | 0.41882 | 0.41882 | 0.41882 | 0.41882 | 0.41882 | 0.41882 | 0.41882 | 0.41882 |  |  | p (psf) | 0.13714 | -1.0286 | -1.2079 | -1.2079 | -0.76681 | -1.1183 | -1.4231 | -1.3693 | -1.0465 | -0.88511 | -1.4231 | -1.3693 | -1.0465 | -0.88511 |  |  | p (psf) | 0.13714 | -1.0286 | -1.2079 | -1.2079 | -0.38533 | -1.1183 | -0.74163 | -0.74163 | -0.74163 | -0.74163 | -0.74163 | -0.74163 | -0.74163 | -0.74163 |  |  | p (psf) | 1.2976 | 0.13187 | -0.047473 | -0.047473 | 0.39364 | 0.042198 | -0.26268 | -0.20888 | 0.11394 | 0.27534 | -0.26268 | -0.20888 | 0.11394 | 0.27534 |  |  | p (psf) | 1.2976 | 0.13187 | -0.047473 | -0.047473 | 0.77512 | 0.042198 | 0.41882 | 0.41882 | 0.41882 | 0.41882 | 0.41882 | 0.41882 | 0.41882 | 0.41882
8 - Areas | [16 empty] | 8 - Areas | [16 empty] | 8 - Areas | [16 empty] | 8 - Areas | [16 empty] | 8 - Areas | [16 empty] | 8 - Areas | [16 empty] | 8 - Areas | [16 empty] | 8 - Areas
Step 8: Calculate surface areas, A, of each building surface | [16 empty] | Step 8: Calculate surface areas, A, of each building surface | [16 empty] | Step 8: Calculate surface areas, A, of each building surface | [16 empty] | Step 8: Calculate surface areas, A, of each building surface | [16 empty] | Step 8: Calculate surface areas, A, of each building surface | [16 empty] | Step 8: Calculate surface areas, A, of each building surface | [16 empty] | Step 8: Calculate surface areas, A, of each building surface | [16 empty] | Step 8: Calculate surface areas, A, of each building surface
| Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y
| Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y
| Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X
| Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X
| Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y
| Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y
| Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X
| Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X
[7 empty] | Dimension parallel to wind direction | L | 40 | 40 | 40 | 40 | [11 empty] | Dimension parallel to wind direction | L | 40 | 40 | 40 | 40 | [11 empty] | Dimension parallel to wind direction | L | 40 | 40 | 40 | 40 | [11 empty] | Dimension parallel to wind direction | L | 40 | 40 | 40 | 40 | [11 empty] | Dimension parallel to wind direction | L | 20 | 20 | 20 | 20 | [11 empty] | Dimension parallel to wind direction | L | 20 | 20 | 20 | 20 | [11 empty] | Dimension parallel to wind direction | L | 20 | 20 | 20 | 20 | [11 empty] | Dimension parallel to wind direction | L | 20 | 20 | 20 | 20
[7 empty] | Dimension perpendicular to wind direction | B | 20 | 20 | 20 | 20 | [11 empty] | Dimension perpendicular to wind direction | B | 20 | 20 | 20 | 20 | [11 empty] | Dimension perpendicular to wind direction | B | 20 | 20 | 20 | 20 | [11 empty] | Dimension perpendicular to wind direction | B | 20 | 20 | 20 | 20 | [11 empty] | Dimension perpendicular to wind direction | B | 40 | 40 | 40 | 40 | [11 empty] | Dimension perpendicular to wind direction | B | 40 | 40 | 40 | 40 | [11 empty] | Dimension perpendicular to wind direction | B | 40 | 40 | 40 | 40 | [11 empty] | Dimension perpendicular to wind direction | B | 40 | 40 | 40 | 40
[7 empty] | Ridge length parallel to wind direction | Ra | 0 | 0 | 0 | 0 | [11 empty] | Ridge length parallel to wind direction | Ra | 0 | 0 | 0 | 0 | [11 empty] | Ridge length parallel to wind direction | Ra | 0 | 0 | 0 | 0 | [11 empty] | Ridge length parallel to wind direction | Ra | 0 | 0 | 0 | 0 | [11 empty] | Ridge length parallel to wind direction | Ra | 0 | 0 | 0 | 0 | [11 empty] | Ridge length parallel to wind direction | Ra | 0 | 0 | 0 | 0 | [11 empty] | Ridge length parallel to wind direction | Ra | 0 | 0 | 0 | 0 | [11 empty] | Ridge length parallel to wind direction | Ra | 0 | 0 | 0 | 0
[7 empty] | Ridge length perpendicular to wind direction | Rb | 0 | 0 | 0 | 0 | [11 empty] | Ridge length perpendicular to wind direction | Rb | 0 | 0 | 0 | 0 | [11 empty] | Ridge length perpendicular to wind direction | Rb | 0 | 0 | 0 | 0 | [11 empty] | Ridge length perpendicular to wind direction | Rb | 0 | 0 | 0 | 0 | [11 empty] | Ridge length perpendicular to wind direction | Rb | 0 | 0 | 0 | 0 | [11 empty] | Ridge length perpendicular to wind direction | Rb | 0 | 0 | 0 | 0 | [11 empty] | Ridge length perpendicular to wind direction | Rb | 0 | 0 | 0 | 0 | [11 empty] | Ridge length perpendicular to wind direction | Rb | 0 | 0 | 0 | 0
[7 empty] | Pitch angle of roof parallel to wind direction |  | 30.9638 | 30.9638 | 30.9638 | 30.9638 | [11 empty] | Pitch angle of roof parallel to wind direction |  | 30.9638 | 30.9638 | 30.9638 | 30.9638 | [11 empty] | Pitch angle of roof parallel to wind direction |  | 30.9638 | 30.9638 | 30.9638 | 30.9638 | [11 empty] | Pitch angle of roof parallel to wind direction |  | 30.9638 | 30.9638 | 30.9638 | 30.9638 | [11 empty] | Pitch angle of roof parallel to wind direction |  | 16.6993 | 16.6993 | 16.6993 | 16.6993 | [11 empty] | Pitch angle of roof parallel to wind direction |  | 16.6993 | 16.6993 | 16.6993 | 16.6993 | [11 empty] | Pitch angle of roof parallel to wind direction |  | 16.6993 | 16.6993 | 16.6993 | 16.6993 | [11 empty] | Pitch angle of roof parallel to wind direction |  | 16.6993 | 16.6993 | 16.6993 | 16.6993
[7 empty] | Pitch angle of roof perpendicular to wind direction |  | 16.6993 | 16.6993 | 16.6993 | 16.6993 | [11 empty] | Pitch angle of roof perpendicular to wind direction |  | 16.6993 | 16.6993 | 16.6993 | 16.6993 | [11 empty] | Pitch angle of roof perpendicular to wind direction |  | 16.6993 | 16.6993 | 16.6993 | 16.6993 | [11 empty] | Pitch angle of roof perpendicular to wind direction |  | 16.6993 | 16.6993 | 16.6993 | 16.6993 | [11 empty] | Pitch angle of roof perpendicular to wind direction |  | 30.9638 | 30.9638 | 30.9638 | 30.9638 | [11 empty] | Pitch angle of roof perpendicular to wind direction |  | 30.9638 | 30.9638 | 30.9638 | 30.9638 | [11 empty] | Pitch angle of roof perpendicular to wind direction |  | 30.9638 | 30.9638 | 30.9638 | 30.9638 | [11 empty] | Pitch angle of roof perpendicular to wind direction |  | 30.9638 | 30.9638 | 30.9638 | 30.9638
[7 empty] | Mean roof height | h | 11 | 11 | 11 | 11 | [11 empty] | Mean roof height | h | 11 | 11 | 11 | 11 | [11 empty] | Mean roof height | h | 11 | 11 | 11 | 11 | [11 empty] | Mean roof height | h | 11 | 11 | 11 | 11 | [11 empty] | Mean roof height | h | 11 | 11 | 11 | 11 | [11 empty] | Mean roof height | h | 11 | 11 | 11 | 11 | [11 empty] | Mean roof height | h | 11 | 11 | 11 | 11 | [11 empty] | Mean roof height | h | 11 | 11 | 11 | 11
[7 empty] | Roof height | rh | 6 | 6 | 6 | 6 | [11 empty] | Roof height | rh | 6 | 6 | 6 | 6 | [11 empty] | Roof height | rh | 6 | 6 | 6 | 6 | [11 empty] | Roof height | rh | 6 | 6 | 6 | 6 | [11 empty] | Roof height | rh | 6 | 6 | 6 | 6 | [11 empty] | Roof height | rh | 6 | 6 | 6 | 6 | [11 empty] | Roof height | rh | 6 | 6 | 6 | 6 | [11 empty] | Roof height | rh | 6 | 6 | 6 | 6
[7 empty] | Distance from windward edge to roof apex | r | 20 | 20 | 20 | 20 | [11 empty] | Distance from windward edge to roof apex | r | 20 | 20 | 20 | 20 | [11 empty] | Distance from windward edge to roof apex | r | 20 | 20 | 20 | 20 | [11 empty] | Distance from windward edge to roof apex | r | 20 | 20 | 20 | 20 | [11 empty] | Distance from windward edge to roof apex | r | 10 | 10 | 10 | 10 | [11 empty] | Distance from windward edge to roof apex | r | 10 | 10 | 10 | 10 | [11 empty] | Distance from windward edge to roof apex | r | 10 | 10 | 10 | 10 | [11 empty] | Distance from windward edge to roof apex | r | 10 | 10 | 10 | 10
[7 empty] | Distance from windward edge to roof apex + ridge length | s | 20 | 20 | 20 | 20 | [11 empty] | Distance from windward edge to roof apex + ridge length | s | 20 | 20 | 20 | 20 | [11 empty] | Distance from windward edge to roof apex + ridge length | s | 20 | 20 | 20 | 20 | [11 empty] | Distance from windward edge to roof apex + ridge length | s | 20 | 20 | 20 | 20 | [11 empty] | Distance from windward edge to roof apex + ridge length | s | 10 | 10 | 10 | 10 | [11 empty] | Distance from windward edge to roof apex + ridge length | s | 10 | 10 | 10 | 10 | [11 empty] | Distance from windward edge to roof apex + ridge length | s | 10 | 10 | 10 | 10 | [11 empty] | Distance from windward edge to roof apex + ridge length | s | 10 | 10 | 10 | 10
[9 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge
[9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h
[9 empty] | Roof Side 1 |  |  |  | Roof Side 2 | [12 empty] | Roof Side 1 |  |  |  | Roof Side 2 | [12 empty] | Roof Side 1 |  |  |  | Roof Side 2 | [12 empty] | Roof Side 1 |  |  |  | Roof Side 2 | [12 empty] | Roof Side 1 |  |  |  | Roof Side 2 | [12 empty] | Roof Side 1 |  |  |  | Roof Side 2 | [12 empty] | Roof Side 1 |  |  |  | Roof Side 2 | [12 empty] | Roof Side 1 |  |  |  | Roof Side 2
[9 empty] | +Y |  |  |  | -Y | [12 empty] | +Y |  |  |  | -Y | [12 empty] | +Y |  |  |  | -Y | [12 empty] | +Y |  |  |  | -Y | [12 empty] | +X |  |  |  | -X | [12 empty] | +X |  |  |  | -X | [12 empty] | +X |  |  |  | -X | [12 empty] | +X |  |  |  | -X
[7 empty] | Distance from leading edge of first boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a1 | 0 | 5.5 | 11 | 22 | [11 empty] | Distance from leading edge of first boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a1 | 0 | 5.5 | 11 | 22 | [11 empty] | Distance from leading edge of first boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a1 | 0 | 5.5 | 11 | 22 | [11 empty] | Distance from leading edge of first boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a1 | 0 | 5.5 | 11 | 22 | [11 empty] | Distance from leading edge of first boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a1 | 0 | 5.5 | 11 | 20 | [11 empty] | Distance from leading edge of first boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a1 | 0 | 5.5 | 11 | 20 | [11 empty] | Distance from leading edge of first boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a1 | 0 | 5.5 | 11 | 20 | [11 empty] | Distance from leading edge of first boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a1 | 0 | 5.5 | 11 | 20
[7 empty] | Horizontal distance perpendicular to a1 to the edge | b1 | 0 | 2.75 | 5.5 | 9 | [12 empty] | b1 | 0 | 2.75 | 5.5 | 9 | [12 empty] | b1 | 0 | 2.75 | 5.5 | 9 | [12 empty] | b1 | 0 | 2.75 | 5.5 | 9 | [12 empty] | b1 | 0 | 11 | 18 | 0 | [12 empty] | b1 | 0 | 11 | 18 | 0 | [12 empty] | b1 | 0 | 11 | 18 | 0 | [12 empty] | b1 | 0 | 11 | 18 | 0
[7 empty] | Area of first trangle | A11 | 0 | 7.5625 | 30.25 | 100 | [11 empty] | Area of first trangle | A11 | 0 | 7.5625 | 30.25 | 100 | [11 empty] | Area of first trangle | A11 | 0 | 7.5625 | 30.25 | 100 | [11 empty] | Area of first trangle | A11 | 0 | 7.5625 | 30.25 | 100 | [11 empty] | Area of first trangle | A11 | 0 | 30.25 | 100 | 100 | [11 empty] | Area of first trangle | A11 | 0 | 30.25 | 100 | 100 | [11 empty] | Area of first trangle | A11 | 0 | 30.25 | 100 | 100 | [11 empty] | Area of first trangle | A11 | 0 | 30.25 | 100 | 100
[7 empty] | Area of first rectangle | A12 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A12 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A12 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A12 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A12 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A12 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A12 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A12 | 0 | 0 | 0 | 0
[7 empty] | Area of top triangular part | A13 | 0 | 0 | 0 | 1 | [11 empty] | Area of top triangular part | A13 | 0 | 0 | 0 | 1 | [11 empty] | Area of top triangular part | A13 | 0 | 0 | 0 | 1 | [11 empty] | Area of top triangular part | A13 | 0 | 0 | 0 | 1 | [11 empty] | Area of top triangular part | A13 | 0 | 0 | 1 | 100 | [11 empty] | Area of top triangular part | A13 | 0 | 0 | 1 | 100 | [11 empty] | Area of top triangular part | A13 | 0 | 0 | 1 | 100 | [11 empty] | Area of top triangular part | A13 | 0 | 0 | 1 | 100
[7 empty] | Area of bottom rectangular part | A14 | 0 | 0 | 0 | 18 | [11 empty] | Area of bottom rectangular part | A14 | 0 | 0 | 0 | 18 | [11 empty] | Area of bottom rectangular part | A14 | 0 | 0 | 0 | 18 | [11 empty] | Area of bottom rectangular part | A14 | 0 | 0 | 0 | 18 | [11 empty] | Area of bottom rectangular part | A14 | 0 | 0 | 18 | 0 | [11 empty] | Area of bottom rectangular part | A14 | 0 | 0 | 18 | 0 | [11 empty] | Area of bottom rectangular part | A14 | 0 | 0 | 18 | 0 | [11 empty] | Area of bottom rectangular part | A14 | 0 | 0 | 18 | 0
[8 empty] | A1 | 0 | 7.5625 | 30.25 | 119 | [12 empty] | A1 | 0 | 7.5625 | 30.25 | 119 | [12 empty] | A1 | 0 | 7.5625 | 30.25 | 119 | [12 empty] | A1 | 0 | 7.5625 | 30.25 | 119 | [12 empty] | A1 | 0 | 30.25 | 119 | 200 | [12 empty] | A1 | 0 | 30.25 | 119 | 200 | [12 empty] | A1 | 0 | 30.25 | 119 | 200 | [12 empty] | A1 | 0 | 30.25 | 119 | 200
[7 empty] | Distance from leading edge to centroid of first triangle | d11 | 0 | 3.6667 | 7.3333 | 13.3333 | [11 empty] | Distance from leading edge to centroid of first triangle | d11 | 0 | 3.6667 | 7.3333 | 13.3333 | [11 empty] | Distance from leading edge to centroid of first triangle | d11 | 0 | 3.6667 | 7.3333 | 13.3333 | [11 empty] | Distance from leading edge to centroid of first triangle | d11 | 0 | 3.6667 | 7.3333 | 13.3333 | [11 empty] | Distance from leading edge to centroid of first triangle | d11 | 0 | 3.6667 | 6.6667 | 6.6667 | [11 empty] | Distance from leading edge to centroid of first triangle | d11 | 0 | 3.6667 | 6.6667 | 6.6667 | [11 empty] | Distance from leading edge to centroid of first triangle | d11 | 0 | 3.6667 | 6.6667 | 6.6667 | [11 empty] | Distance from leading edge to centroid of first triangle | d11 | 0 | 3.6667 | 6.6667 | 6.6667
[7 empty] | Distance from leading edge to centroid of first rectangle | d12 | 0 | 0 | 0 | 20 | [11 empty] | Distance from leading edge to centroid of first rectangle | d12 | 0 | 0 | 0 | 20 | [11 empty] | Distance from leading edge to centroid of first rectangle | d12 | 0 | 0 | 0 | 20 | [11 empty] | Distance from leading edge to centroid of first rectangle | d12 | 0 | 0 | 0 | 20 | [11 empty] | Distance from leading edge to centroid of first rectangle | d12 | 0 | 0 | 10 | 10 | [11 empty] | Distance from leading edge to centroid of first rectangle | d12 | 0 | 0 | 10 | 10 | [11 empty] | Distance from leading edge to centroid of first rectangle | d12 | 0 | 0 | 10 | 10 | [11 empty] | Distance from leading edge to centroid of first rectangle | d12 | 0 | 0 | 10 | 10
[7 empty] | Distance from leading edge to centroid of top triangular part | d13 | 0 | 0 | 0 | 20.6667 | [11 empty] | Distance from leading edge to centroid of top triangular part | d13 | 0 | 0 | 0 | 20.6667 | [11 empty] | Distance from leading edge to centroid of top triangular part | d13 | 0 | 0 | 0 | 20.6667 | [11 empty] | Distance from leading edge to centroid of top triangular part | d13 | 0 | 0 | 0 | 20.6667 | [11 empty] | Distance from leading edge to centroid of top triangular part | d13 | 0 | 0 | 10.3333 | 13.3333 | [11 empty] | Distance from leading edge to centroid of top triangular part | d13 | 0 | 0 | 10.3333 | 13.3333 | [11 empty] | Distance from leading edge to centroid of top triangular part | d13 | 0 | 0 | 10.3333 | 13.3333 | [11 empty] | Distance from leading edge to centroid of top triangular part | d13 | 0 | 0 | 10.3333 | 13.3333
[7 empty] | Distance from leading edge to centroid of bottom rectangular part | d14 | 0 | 0 | 0 | 21 | [11 empty] | Distance from leading edge to centroid of bottom rectangular part | d14 | 0 | 0 | 0 | 21 | [11 empty] | Distance from leading edge to centroid of bottom rectangular part | d14 | 0 | 0 | 0 | 21 | [11 empty] | Distance from leading edge to centroid of bottom rectangular part | d14 | 0 | 0 | 0 | 21 | [11 empty] | Distance from leading edge to centroid of bottom rectangular part | d14 | 0 | 0 | 10.5 | 15 | [11 empty] | Distance from leading edge to centroid of bottom rectangular part | d14 | 0 | 0 | 10.5 | 15 | [11 empty] | Distance from leading edge to centroid of bottom rectangular part | d14 | 0 | 0 | 10.5 | 15 | [11 empty] | Distance from leading edge to centroid of bottom rectangular part | d14 | 0 | 0 | 10.5 | 15
[8 empty] | d1 | 0 | 3.6667 | 7.3333 | 14.5546 | [12 empty] | d1 | 0 | 3.6667 | 7.3333 | 14.5546 | [12 empty] | d1 | 0 | 3.6667 | 7.3333 | 14.5546 | [12 empty] | d1 | 0 | 3.6667 | 7.3333 | 14.5546 | [12 empty] | d1 | 0 | 3.6667 | 7.2773 | 10 | [12 empty] | d1 | 0 | 3.6667 | 7.2773 | 10 | [12 empty] | d1 | 0 | 3.6667 | 7.2773 | 10 | [12 empty] | d1 | 0 | 3.6667 | 7.2773 | 10
[7 empty] | Distance from leading edge of second boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a2 | 5.5 | 11 | 22 | 40 | [11 empty] | Distance from leading edge of second boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a2 | 5.5 | 11 | 22 | 40 | [11 empty] | Distance from leading edge of second boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a2 | 5.5 | 11 | 22 | 40 | [11 empty] | Distance from leading edge of second boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a2 | 5.5 | 11 | 22 | 40 | [11 empty] | Distance from leading edge of second boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a2 | 5.5 | 11 | 20 | 20 | [11 empty] | Distance from leading edge of second boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a2 | 5.5 | 11 | 20 | 20 | [11 empty] | Distance from leading edge of second boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a2 | 5.5 | 11 | 20 | 20 | [11 empty] | Distance from leading edge of second boundary (e.g., h/2) of area of interest (e.g., h/2-h) | a2 | 5.5 | 11 | 20 | 20
[8 empty] | b2 | 2.75 | 5.5 | 9 | 0 | [12 empty] | b2 | 2.75 | 5.5 | 9 | 0 | [12 empty] | b2 | 2.75 | 5.5 | 9 | 0 | [12 empty] | b2 | 2.75 | 5.5 | 9 | 0 | [12 empty] | b2 | 11 | 18 | 0 | 0 | [12 empty] | b2 | 11 | 18 | 0 | 0 | [12 empty] | b2 | 11 | 18 | 0 | 0 | [12 empty] | b2 | 11 | 18 | 0 | 0
[7 empty] | Area of first trangle | A21 | 7.5625 | 30.25 | 100 | 100 | [11 empty] | Area of first trangle | A21 | 7.5625 | 30.25 | 100 | 100 | [11 empty] | Area of first trangle | A21 | 7.5625 | 30.25 | 100 | 100 | [11 empty] | Area of first trangle | A21 | 7.5625 | 30.25 | 100 | 100 | [11 empty] | Area of first trangle | A21 | 30.25 | 100 | 100 | 100 | [11 empty] | Area of first trangle | A21 | 30.25 | 100 | 100 | 100 | [11 empty] | Area of first trangle | A21 | 30.25 | 100 | 100 | 100 | [11 empty] | Area of first trangle | A21 | 30.25 | 100 | 100 | 100
[7 empty] | Area of first rectangle | A22 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A22 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A22 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A22 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A22 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A22 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A22 | 0 | 0 | 0 | 0 | [11 empty] | Area of first rectangle | A22 | 0 | 0 | 0 | 0
[7 empty] | Area of top triangular part | A23 | 0 | 0 | 1 | 100 | [11 empty] | Area of top triangular part | A23 | 0 | 0 | 1 | 100 | [11 empty] | Area of top triangular part | A23 | 0 | 0 | 1 | 100 | [11 empty] | Area of top triangular part | A23 | 0 | 0 | 1 | 100 | [11 empty] | Area of top triangular part | A23 | 0 | 1 | 100 | 100 | [11 empty] | Area of top triangular part | A23 | 0 | 1 | 100 | 100 | [11 empty] | Area of top triangular part | A23 | 0 | 1 | 100 | 100 | [11 empty] | Area of top triangular part | A23 | 0 | 1 | 100 | 100
[7 empty] | Area of bottom rectangular part | A24 | 0 | 0 | 18 | 0 | [11 empty] | Area of bottom rectangular part | A24 | 0 | 0 | 18 | 0 | [11 empty] | Area of bottom rectangular part | A24 | 0 | 0 | 18 | 0 | [11 empty] | Area of bottom rectangular part | A24 | 0 | 0 | 18 | 0 | [11 empty] | Area of bottom rectangular part | A24 | 0 | 18 | 0 | 0 | [11 empty] | Area of bottom rectangular part | A24 | 0 | 18 | 0 | 0 | [11 empty] | Area of bottom rectangular part | A24 | 0 | 18 | 0 | 0 | [11 empty] | Area of bottom rectangular part | A24 | 0 | 18 | 0 | 0
[8 empty] | A2 | 7.5625 | 30.25 | 119 | 200 | [12 empty] | A2 | 7.5625 | 30.25 | 119 | 200 | [12 empty] | A2 | 7.5625 | 30.25 | 119 | 200 | [12 empty] | A2 | 7.5625 | 30.25 | 119 | 200 | [12 empty] | A2 | 30.25 | 119 | 200 | 200 | [12 empty] | A2 | 30.25 | 119 | 200 | 200 | [12 empty] | A2 | 30.25 | 119 | 200 | 200 | [12 empty] | A2 | 30.25 | 119 | 200 | 200
[8 empty] | d21 | 3.6667 | 7.3333 | 13.3333 | 13.3333 | [12 empty] | d21 | 3.6667 | 7.3333 | 13.3333 | 13.3333 | [12 empty] | d21 | 3.6667 | 7.3333 | 13.3333 | 13.3333 | [12 empty] | d21 | 3.6667 | 7.3333 | 13.3333 | 13.3333 | [12 empty] | d21 | 3.6667 | 6.6667 | 6.6667 | 6.6667 | [12 empty] | d21 | 3.6667 | 6.6667 | 6.6667 | 6.6667 | [12 empty] | d21 | 3.6667 | 6.6667 | 6.6667 | 6.6667 | [12 empty] | d21 | 3.6667 | 6.6667 | 6.6667 | 6.6667
[6 empty] | Horizontal roof area | 200 | d22 | 0 | 0 | 20 | 20 | [10 empty] | Horizontal roof area | 200 | d22 | 0 | 0 | 20 | 20 | [10 empty] | Horizontal roof area | 200 | d22 | 0 | 0 | 20 | 20 | [10 empty] | Horizontal roof area | 200 | d22 | 0 | 0 | 20 | 20 | [10 empty] | Horizontal roof area | 200 | d22 | 0 | 10 | 10 | 10 | [10 empty] | Horizontal roof area | 200 | d22 | 0 | 10 | 10 | 10 | [10 empty] | Horizontal roof area | 200 | d22 | 0 | 10 | 10 | 10 | [10 empty] | Horizontal roof area | 200 | d22 | 0 | 10 | 10 | 10
[6 empty] | Roof area | 233.2381 | d23 | 0 | 0 | 20.6667 | 26.6667 | [10 empty] | Roof area | 233.2381 | d23 | 0 | 0 | 20.6667 | 26.6667 | [10 empty] | Roof area | 233.2381 | d23 | 0 | 0 | 20.6667 | 26.6667 | [10 empty] | Roof area | 233.2381 | d23 | 0 | 0 | 20.6667 | 26.6667 | [10 empty] | Roof area | 208.8061 | d23 | 0 | 10.3333 | 13.3333 | 13.3333 | [10 empty] | Roof area | 208.8061 | d23 | 0 | 10.3333 | 13.3333 | 13.3333 | [10 empty] | Roof area | 208.8061 | d23 | 0 | 10.3333 | 13.3333 | 13.3333 | [10 empty] | Roof area | 208.8061 | d23 | 0 | 10.3333 | 13.3333 | 13.3333
[8 empty] | d24 | 0 | 0 | 21 | 30 | [12 empty] | d24 | 0 | 0 | 21 | 30 | [12 empty] | d24 | 0 | 0 | 21 | 30 | [12 empty] | d24 | 0 | 0 | 21 | 30 | [12 empty] | d24 | 0 | 10.5 | 15 | 15 | [12 empty] | d24 | 0 | 10.5 | 15 | 15 | [12 empty] | d24 | 0 | 10.5 | 15 | 15 | [12 empty] | d24 | 0 | 10.5 | 15 | 15
[8 empty] | d2 | 3.6667 | 7.3333 | 14.5546 | 20 | [12 empty] | d2 | 3.6667 | 7.3333 | 14.5546 | 20 | [12 empty] | d2 | 3.6667 | 7.3333 | 14.5546 | 20 | [12 empty] | d2 | 3.6667 | 7.3333 | 14.5546 | 20 | [12 empty] | d2 | 3.6667 | 7.2773 | 10 | 10 | [12 empty] | d2 | 3.6667 | 7.2773 | 10 | 10 | [12 empty] | d2 | 3.6667 | 7.2773 | 10 | 10 | [12 empty] | d2 | 3.6667 | 7.2773 | 10 | 10
[8 empty] | Horizontal area | 7.5625 | 22.6875 | 88.75 | 81 | [12 empty] | Horizontal area | 7.5625 | 22.6875 | 88.75 | 81 | [12 empty] | Horizontal area | 7.5625 | 22.6875 | 88.75 | 81 | [12 empty] | Horizontal area | 7.5625 | 22.6875 | 88.75 | 81 | [12 empty] | Horizontal area | 30.25 | 88.75 | 81 | 0 | [12 empty] | Horizontal area | 30.25 | 88.75 | 81 | 0 | [12 empty] | Horizontal area | 30.25 | 88.75 | 81 | 0 | [12 empty] | Horizontal area | 30.25 | 88.75 | 81 | 0
[7 empty] | Area | (ft2) | 8.8193 | 26.4579 | 103.4994 | 94.4614 | 8.8193 | 26.4579 | 103.4994 | 94.4614 | [7 empty] | Area | (ft2) | 8.8193 | 26.4579 | 103.4994 | 94.4614 | 8.8193 | 26.4579 | 103.4994 | 94.4614 | [7 empty] | Area | (ft2) | 8.8193 | 26.4579 | 103.4994 | 94.4614 | 8.8193 | 26.4579 | 103.4994 | 94.4614 | [7 empty] | Area | (ft2) | 8.8193 | 26.4579 | 103.4994 | 94.4614 | 8.8193 | 26.4579 | 103.4994 | 94.4614 | [7 empty] | Area | (ft2) | 31.5819 | 92.6577 | 84.5665 | 0 | 31.5819 | 92.6577 | 84.5665 | 0 | [7 empty] | Area | (ft2) | 31.5819 | 92.6577 | 84.5665 | 0 | 31.5819 | 92.6577 | 84.5665 | 0 | [7 empty] | Area | (ft2) | 31.5819 | 92.6577 | 84.5665 | 0 | 31.5819 | 92.6577 | 84.5665 | 0 | [7 empty] | Area | (ft2) | 31.5819 | 92.6577 | 84.5665 | 0 | 31.5819 | 92.6577 | 84.5665 | 0
[8 empty] | Distance b/t center of force and windward edge | 3.6667 | 8.5556 | 17.016 | 28 | 3.6667 | 8.5556 | 17.016 | 28 | [8 empty] | Distance b/t center of force and windward edge | 3.6667 | 8.5556 | 17.016 | 28 | 3.6667 | 8.5556 | 17.016 | 28 | [8 empty] | Distance b/t center of force and windward edge | 3.6667 | 8.5556 | 17.016 | 28 | 3.6667 | 8.5556 | 17.016 | 28 | [8 empty] | Distance b/t center of force and windward edge | 3.6667 | 8.5556 | 17.016 | 28 | 3.6667 | 8.5556 | 17.016 | 28 | [8 empty] | Distance b/t center of force and windward edge | 3.6667 | 8.508 | 14 | 0 | 3.6667 | 8.508 | 14 | 0 | [8 empty] | Distance b/t center of force and windward edge | 3.6667 | 8.508 | 14 | 0 | 3.6667 | 8.508 | 14 | 0 | [8 empty] | Distance b/t center of force and windward edge | 3.6667 | 8.508 | 14 | 0 | 3.6667 | 8.508 | 14 | 0 | [8 empty] | Distance b/t center of force and windward edge | 3.6667 | 8.508 | 14 | 0 | 3.6667 | 8.508 | 14 | 0
[9 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge
[9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h
|  |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2
|  |  | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X
| Area | (ft2) | 160 | 160 | 320 | 320 | 208.8061 | 208.8061 | 8.8193 | 26.4579 | 103.4994 | 94.4614 | 8.8193 | 26.4579 | 103.4994 | 94.4614 |  | Area | (ft2) | 160 | 160 | 320 | 320 | 208.8061 | 208.8061 | 8.8193 | 26.4579 | 103.4994 | 94.4614 | 8.8193 | 26.4579 | 103.4994 | 94.4614 |  | Area | (ft2) | 160 | 160 | 320 | 320 | 208.8061 | 208.8061 | 8.8193 | 26.4579 | 103.4994 | 94.4614 | 8.8193 | 26.4579 | 103.4994 | 94.4614 |  | Area | (ft2) | 160 | 160 | 320 | 320 | 208.8061 | 208.8061 | 8.8193 | 26.4579 | 103.4994 | 94.4614 | 8.8193 | 26.4579 | 103.4994 | 94.4614 |  | Area | (ft2) | 320 | 320 | 160 | 160 | 233.2381 | 233.2381 | 31.5819 | 92.6577 | 84.5665 | 0 | 31.5819 | 92.6577 | 84.5665 | 0 |  | Area | (ft2) | 320 | 320 | 160 | 160 | 233.2381 | 233.2381 | 31.5819 | 92.6577 | 84.5665 | 0 | 31.5819 | 92.6577 | 84.5665 | 0 |  | Area | (ft2) | 320 | 320 | 160 | 160 | 233.2381 | 233.2381 | 31.5819 | 92.6577 | 84.5665 | 0 | 31.5819 | 92.6577 | 84.5665 | 0 |  | Area | (ft2) | 320 | 320 | 160 | 160 | 233.2381 | 233.2381 | 31.5819 | 92.6577 | 84.5665 | 0 | 31.5819 | 92.6577 | 84.5665 | 0
| Distance b/t center of force and windward edge | (ft) | [6 empty] | 3.6667 | 8.5556 | 17.016 | 28 | 3.6667 | 8.5556 | 17.016 | 28 |  | Distance b/t center of force and windward edge | (ft) | [6 empty] | 3.6667 | 8.5556 | 17.016 | 28 | 3.6667 | 8.5556 | 17.016 | 28 |  | Distance b/t center of force and windward edge | (ft) | [6 empty] | 3.6667 | 8.5556 | 17.016 | 28 | 3.6667 | 8.5556 | 17.016 | 28 |  | Distance b/t center of force and windward edge | (ft) | [6 empty] | 3.6667 | 8.5556 | 17.016 | 28 | 3.6667 | 8.5556 | 17.016 | 28 |  | Distance b/t center of force and windward edge | (ft) | [6 empty] | 3.6667 | 8.508 | 14 | 0 | 3.6667 | 8.508 | 14 | 0 |  | Distance b/t center of force and windward edge | (ft) | [6 empty] | 3.6667 | 8.508 | 14 | 0 | 3.6667 | 8.508 | 14 | 0 |  | Distance b/t center of force and windward edge | (ft) | [6 empty] | 3.6667 | 8.508 | 14 | 0 | 3.6667 | 8.508 | 14 | 0 |  | Distance b/t center of force and windward edge | (ft) | [6 empty] | 3.6667 | 8.508 | 14 | 0 | 3.6667 | 8.508 | 14 | 0
IF GABLE ROOF
| Area | (ft2)
| Distance b/t center of force and windward edge | (ft)
9.1 - FORCES FOR OPEN | [16 empty] | 9.1 - FORCES FOR OPEN | [16 empty] | 9.1 - FORCES FOR OPEN | [16 empty] | 9.1 - FORCES FOR OPEN | [16 empty] | 9.1 - FORCES FOR OPEN | [16 empty] | 9.1 - FORCES FOR OPEN | [16 empty] | 9.1 - FORCES FOR OPEN | [16 empty] | 9.1 - FORCES FOR OPEN
Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface
| Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y
| Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y
| Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X
| Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X
| Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y
| Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y
| Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X
| Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X
| Dimension parallel to wind direction | 40 | [15 empty] | Dimension parallel to wind direction | 40 | [15 empty] | Dimension parallel to wind direction | 40 | [15 empty] | Dimension parallel to wind direction | 40 | [15 empty] | Dimension parallel to wind direction | 20 | [15 empty] | Dimension parallel to wind direction | 20 | [15 empty] | Dimension parallel to wind direction | 20 | [15 empty] | Dimension parallel to wind direction | 20
| Dimension perpendicular to wind direction | 20 | [15 empty] | Dimension perpendicular to wind direction | 20 | [15 empty] | Dimension perpendicular to wind direction | 20 | [15 empty] | Dimension perpendicular to wind direction | 20 | [15 empty] | Dimension perpendicular to wind direction | 40 | [15 empty] | Dimension perpendicular to wind direction | 40 | [15 empty] | Dimension perpendicular to wind direction | 40 | [15 empty] | Dimension perpendicular to wind direction | 40
| Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0
| Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0
| Pitch angle of roof parallel to wind direction | 30.9638 | [15 empty] | Pitch angle of roof parallel to wind direction | 30.9638 | [15 empty] | Pitch angle of roof parallel to wind direction | 30.9638 | [15 empty] | Pitch angle of roof parallel to wind direction | 30.9638 | [15 empty] | Pitch angle of roof parallel to wind direction | 16.6993 | [15 empty] | Pitch angle of roof parallel to wind direction | 16.6993 | [15 empty] | Pitch angle of roof parallel to wind direction | 16.6993 | [15 empty] | Pitch angle of roof parallel to wind direction | 16.6993
| Pitch angle of roof perpendicular to wind direction | 16.6993 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 16.6993 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 16.6993 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 16.6993 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 30.9638 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 30.9638 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 30.9638 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 30.9638
| Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8
| Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11
| Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6
| OPEN | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | OPEN | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | OPEN | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | OPEN | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | OPEN | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | OPEN | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | OPEN | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | OPEN | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge
[9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h
|  |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2
|  |  | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X
| X-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.28735 | 0.28735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.28735 | 0.28735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.28735 | 0.28735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.28735 | 0.28735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.28735 | -0.28735 | -0.28735 | -0.28735 | 0.28735 | 0.28735 | 0.28735 | 0.28735 |  | X-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.28735 | -0.28735 | -0.28735 | -0.28735 | 0.28735 | 0.28735 | 0.28735 | 0.28735 |  | X-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.28735 | -0.28735 | -0.28735 | -0.28735 | 0.28735 | 0.28735 | 0.28735 | 0.28735 |  | X-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.28735 | -0.28735 | -0.28735 | -0.28735 | 0.28735 | 0.28735 | 0.28735 | 0.28735
| Y-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.5145 | 0.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Y-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.5145 | 0.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Y-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.5145 | 0.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Y-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.5145 | 0.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.95783 | -0.95783 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.95783 | -0.95783 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.95783 | -0.95783 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.95783 | -0.95783 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.85749 | -0.85749 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.85749 | -0.85749 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.85749 | -0.85749 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.85749 | -0.85749 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783
| Overturn moment arm for X component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Overturn moment arm for Y component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Overturn moment arm for Z component | ft | 40 | 0 |  |  | 33.3333 | 6.6667 | 36.3333 | 31.4444 | 22.984 | 12 | 36.3333 | 31.4444 | 22.984 | 12 |  | Overturn moment arm for Z component | ft | 40 | 0 |  |  | 33.3333 | 6.6667 | 36.3333 | 31.4444 | 22.984 | 12 | 36.3333 | 31.4444 | 22.984 | 12 |  | Overturn moment arm for Z component | ft | 40 | 0 |  |  | 33.3333 | 6.6667 | 36.3333 | 31.4444 | 22.984 | 12 | 36.3333 | 31.4444 | 22.984 | 12 |  | Overturn moment arm for Z component | ft | 40 | 0 |  |  | 33.3333 | 6.6667 | 36.3333 | 31.4444 | 22.984 | 12 | 36.3333 | 31.4444 | 22.984 | 12 |  | Overturn moment arm for Z component | ft | 0 | 0 |  |  | 16.6667 | 3.3333 | 16.3333 | 11.492 | 6 | 20 | 16.3333 | 11.492 | 6 | 20 |  | Overturn moment arm for Z component | ft | 0 | 0 |  |  | 16.6667 | 3.3333 | 16.3333 | 11.492 | 6 | 20 | 16.3333 | 11.492 | 6 | 20 |  | Overturn moment arm for Z component | ft | 0 | 0 |  |  | 16.6667 | 3.3333 | 16.3333 | 11.492 | 6 | 20 | 16.3333 | 11.492 | 6 | 20 |  | Overturn moment arm for Z component | ft | 0 | 0 |  |  | 16.6667 | 3.3333 | 16.3333 | 11.492 | 6 | 20 | 16.3333 | 11.492 | 6 | 20
| Horizontal force (+ in X) | lbs | -2.7429 | -16.9848 |  |  | -59.183 | -15.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in X) | lbs | -2.7429 | -16.9848 |  |  | -2.9423 | -55.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in X) | lbs | -25.9519 | 6.2242 |  |  | 64.5633 | -56.2407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in X) | lbs | -25.9519 | 6.2242 |  |  | 34.7196 | -87.3033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in X) | lbs | 0 | 0 |  |  | 0 | 0 | 6.5101 | 19.1 | 13.0741 | 0 | -6.5101 | -19.1 | -13.0741 | 0 |  | Horizontal force (+ in X) | lbs | 0 | 0 |  |  | 0 | 0 | -6.5101 | -19.1 | -10.895 | 0 | 6.5101 | 19.1 | 10.895 | 0 |  | Horizontal force (+ in X) | lbs | 0 | 0 |  |  | 0 | 0 | 9.7652 | 28.6499 | 19.6111 | 0 | -9.7652 | -28.6499 | -19.6111 | 0 |  | Horizontal force (+ in X) | lbs | 0 | 0 |  |  | 0 | 0 | -4.0688 | -11.9375 | -10.895 | 0 | 4.0688 | 11.9375 | 10.895 | 0
| Horizontal force (+ in Y) | lbs | 0 | 0 |  |  | 0 | 0 | 3.2551 | 9.7652 | 28.6499 | 13.0741 | -3.2551 | -9.7652 | -28.6499 | -13.0741 |  | Horizontal force (+ in Y) | lbs | 0 | 0 |  |  | 0 | 0 | -3.2551 | -9.7652 | -23.875 | -13.0741 | 3.2551 | 9.7652 | 23.875 | 13.0741 |  | Horizontal force (+ in Y) | lbs | 0 | 0 |  |  | 0 | 0 | 4.8826 | 14.6478 | 42.9749 | 26.1481 | -4.8826 | -14.6478 | -42.9749 | -26.1481 |  | Horizontal force (+ in Y) | lbs | 0 | 0 |  |  | 0 | 0 | -2.0344 | -6.1032 | -23.875 | -13.0741 | 2.0344 | 6.1032 | 23.875 | 13.0741 |  | Horizontal force (+ in Y) | lbs | -5.4858 | -41.1432 |  |  | -139.887 | 36.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in Y) | lbs | -5.4858 | -41.1432 |  |  | 12.1433 | -92.6965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in Y) | lbs | -51.9038 | 5.2748 |  |  | 73.941 | -73.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in Y) | lbs | -51.9038 | 5.2748 |  |  | 22.9039 | -115.6004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vertical force (+ in Z) | lbs | 0 | 0 |  |  | -197.2766 | 51.4203 | 5.4251 | 16.2753 | 47.7499 | 21.7901 | 5.4251 | 16.2753 | 47.7499 | 21.7901 |  | Vertical force (+ in Z) | lbs | 0 | 0 |  |  | -9.8076 | 185.0866 | -5.4251 | -16.2753 | -39.7916 | -21.7901 | -5.4251 | -16.2753 | -39.7916 | -21.7901 |  | Vertical force (+ in Z) | lbs | 0 | 0 |  |  | 215.2108 | 187.469 | 8.1377 | 24.413 | 71.6249 | 43.5802 | 8.1377 | 24.413 | 71.6249 | 43.5802 |  | Vertical force (+ in Z) | lbs | 0 | 0 |  |  | 115.7321 | 291.0111 | -3.3907 | -10.1721 | -39.7916 | -21.7901 | -3.3907 | -10.1721 | -39.7916 | -21.7901 |  | Vertical force (+ in Z) | lbs | 0 | 0 |  |  | -233.1451 | -60.7166 | 21.7004 | 63.6665 | 43.5802 | 0 | 21.7004 | 63.6665 | 43.5802 | 0 |  | Vertical force (+ in Z) | lbs | 0 | 0 |  |  | 20.2389 | 154.4942 | -21.7004 | -63.6665 | -36.3168 | 0 | -21.7004 | -63.6665 | -36.3168 | 0 |  | Vertical force (+ in Z) | lbs | 0 | 0 |  |  | 123.235 | 123.235 | 32.5506 | 95.4998 | 65.3703 | 0 | 32.5506 | 95.4998 | 65.3703 | 0 |  | Vertical force (+ in Z) | lbs | 0 | 0 |  |  | 38.1731 | 192.6673 | -13.5628 | -39.7916 | -36.3168 | 0 | -13.5628 | -39.7916 | -36.3168 | 0
| Overturn moment | lbs.ft | -20.5716 | -127.3858 |  |  | 5984.0568 | -497.0633 | -197.1122 | -511.7684 | -1097.4856 | -261.4812 | -197.1122 | -511.7684 | -1097.4856 | -261.4812 |  | Overturn moment | lbs.ft | -20.5716 | -127.3858 |  |  | 297.4971 | -1789.1708 | 197.1122 | 511.7684 | 914.5713 | 261.4812 | 197.1122 | 511.7684 | 914.5713 | 261.4812 |  | Overturn moment | lbs.ft | -194.6392 | 46.6818 |  |  | -6528.062 | -1812.2004 | -295.6683 | -767.6526 | -1646.2284 | -522.9623 | -295.6683 | -767.6526 | -1646.2284 | -522.9623 |  | Overturn moment | lbs.ft | -194.6392 | 46.6818 |  |  | -3510.5391 | -2813.1073 | 123.1951 | 319.8552 | 914.5713 | 261.4812 | 123.1951 | 319.8552 | 914.5713 | 261.4812 |  | Overturn moment | lbs.ft | 41.1432 | 308.5744 |  |  | -2486.8808 | -566.6882 | 354.4403 | 731.6571 | 261.4812 | 0 | 354.4403 | 731.6571 | 261.4812 | 0 |  | Overturn moment | lbs.ft | 41.1432 | 308.5744 |  |  | 215.8812 | 1441.9463 | -354.4403 | -731.6571 | -217.901 | 0 | -354.4403 | -731.6571 | -217.901 | 0 |  | Overturn moment | lbs.ft | 389.2784 | -39.5608 |  |  | 1314.5069 | 1150.1936 | 531.6604 | 1097.4856 | 392.2217 | 0 | 531.6604 | 1097.4856 | 392.2217 | 0 |  | Overturn moment | lbs.ft | 389.2784 | -39.5608 |  |  | 407.1797 | 1798.2285 | -221.5252 | -457.2857 | -217.901 | 0 | -221.5252 | -457.2857 | -217.901 | 0
| Total horizontal force (+ in X) | lbs | -94.3367 | [14 empty] | Total horizontal force (+ in X) | lbs | -78.1959 | [14 empty] | Total horizontal force (+ in X) | lbs | -11.4051 | [14 empty] | Total horizontal force (+ in X) | lbs | -72.3114 | [14 empty] | Total horizontal force (+ in X) | lbs | 3.5527e-15 | [14 empty] | Total horizontal force (+ in X) | lbs | -3.5527e-15 | [14 empty] | Total horizontal force (+ in X) | lbs | 3.5527e-15 | [14 empty] | Total horizontal force (+ in X) | lbs | 1.7764e-15
| Total horizontal force (+ in Y) | lbs | 0 |  | Highlighted section is for valence from prorated wall forces of partially enclosed | [12 empty] | Total horizontal force (+ in Y) | lbs | 0 |  | Highlighted section is for valence from prorated wall forces of partially enclosed | [12 empty] | Total horizontal force (+ in Y) | lbs | 0 |  | Highlighted section is for valence from prorated wall forces of partially enclosed | [12 empty] | Total horizontal force (+ in Y) | lbs | 0 |  | Highlighted section is for valence from prorated wall forces of partially enclosed | [12 empty] | Total horizontal force (+ in Y) | lbs | -150.0861 |  | Highlighted section is for valence from prorated wall forces of partially enclosed | [12 empty] | Total horizontal force (+ in Y) | lbs | -127.1822 |  | Highlighted section is for valence from prorated wall forces of partially enclosed | [12 empty] | Total horizontal force (+ in Y) | lbs | -46.629 |  | Highlighted section is for valence from prorated wall forces of partially enclosed | [12 empty] | Total horizontal force (+ in Y) | lbs | -139.3256 |  | Highlighted section is for valence from prorated wall forces of partially enclosed
| Total vertical force (+ in Z) | lbs | 36.6246 | [14 empty] | Total vertical force (+ in Z) | lbs | 8.7148 | [14 empty] | Total vertical force (+ in Z) | lbs | 698.1912 | [14 empty] | Total vertical force (+ in Z) | lbs | 256.4543 | [14 empty] | Total vertical force (+ in Z) | lbs | -35.9673 | [14 empty] | Total vertical force (+ in Z) | lbs | -68.6345 | [14 empty] | Total vertical force (+ in Z) | lbs | 633.3115 | [14 empty] | Total vertical force (+ in Z) | lbs | 51.4981
| Overturn moment | lbs.ft | 1203.3414 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 2130.2349 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -14953.243 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -3233.3981 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -8.6943 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -600.4515 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 6857.1537 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 761.7023 | Must be POSITIVE for overturn
[9 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge
|  |  | Valence | [5 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h |  |  |  | Valence | [5 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h |  |  |  | Valence | [5 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h |  |  |  | Valence | [5 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h |  |  |  | Valence | [5 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h |  |  |  | Valence | [5 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h |  |  |  | Valence | [5 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h |  |  |  | Valence | [5 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h
| IF GABLE ROOF |  | WinWall | LeeWall |  |  | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall |  |  | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall |  |  | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall |  |  | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall |  |  | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall |  |  | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall |  |  | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall |  |  | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2
|  |  | +X | -X |  |  | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X |  |  | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X |  |  | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X |  |  | +X | -X | +Y |  |  |  | -Y | [6 empty] | +Y | -Y |  |  | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y |  |  | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y |  |  | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y |  |  | +Y | -Y | +X |  |  |  | -X
| Length of rectangle in y-direction | ft | [6 empty] | 5.5 | 5.5 | 11 | 18 | [5 empty] | Length of rectangle in y-direction | ft | [6 empty] | 5.5 | 5.5 | 11 | 18 | [5 empty] | Length of rectangle in y-direction | ft | [6 empty] | 5.5 | 5.5 | 11 | 18 | [5 empty] | Length of rectangle in y-direction | ft | [6 empty] | 5.5 | 5.5 | 11 | 18 | [5 empty] | Length of rectangle in y-direction | ft | [15 empty] | Length of rectangle in y-direction | ft | [15 empty] | Length of rectangle in y-direction | ft | [15 empty] | Length of rectangle in y-direction | ft
| Areas | ft2 | 20 | 20 |  |  | 60 | 60 | 64.1405 | 64.1405 | 128.2809 | 209.9143 | 64.1405 | 64.1405 | 128.2809 | 209.9143 |  | Areas | ft2 | 20 | 20 |  |  | 60 | 60 | 64.1405 | 64.1405 | 128.2809 | 209.9143 | 64.1405 | 64.1405 | 128.2809 | 209.9143 |  | Areas | ft2 | 20 | 20 |  |  | 60 | 60 | 64.1405 | 64.1405 | 128.2809 | 209.9143 | 64.1405 | 64.1405 | 128.2809 | 209.9143 |  | Areas | ft2 | 20 | 20 |  |  | 60 | 60 | 64.1405 | 64.1405 | 128.2809 | 209.9143 | 64.1405 | 64.1405 | 128.2809 | 209.9143 |  | Areas | ft2 | 40 | 40 |  |  | 233.2381 | 233.2381 | [9 empty] | Areas | ft2 | 40 | 40 |  |  | 233.2381 | 233.2381 | [9 empty] | Areas | ft2 | 40 | 40 |  |  | 233.2381 | 233.2381 | [9 empty] | Areas | ft2 | 40 | 40 |  |  | 233.2381 | 233.2381
| X-component of normal vector (+inward) |  | -1 | 1 |  |  | -1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | -1 | 1 |  |  | -1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | -1 | 1 |  |  | -1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | -1 | 1 |  |  | -1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | [9 empty] | X-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | [9 empty] | X-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | [9 empty] | X-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0
| Y-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.5145 | 0.5145 | [9 empty] | Y-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.5145 | 0.5145 | [9 empty] | Y-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.5145 | 0.5145 | [9 empty] | Y-component of normal vector (+inward) |  | -1 | 1 |  |  | -0.5145 | 0.5145
| Z-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | 0 | 0 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.85749 | -0.85749 | [9 empty] | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.85749 | -0.85749 | [9 empty] | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.85749 | -0.85749 | [9 empty] | Z-component of normal vector (+inward) |  | 0 | 0 |  |  | -0.85749 | -0.85749
| Overturn moment arm for X component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 7.5 | 7.5 |  |  | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 0 | 0 |  |  | 0 | 0 | [9 empty] | Overturn moment arm for X component | ft | 0 | 0 |  |  | 0 | 0 | [9 empty] | Overturn moment arm for X component | ft | 0 | 0 |  |  | 0 | 0 | [9 empty] | Overturn moment arm for X component | ft | 0 | 0 |  |  | 0 | 0
| Overturn moment arm for Y component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 7.5 | 7.5 |  |  | 11 | 11 | [9 empty] | Overturn moment arm for Y component | ft | 7.5 | 7.5 |  |  | 11 | 11 | [9 empty] | Overturn moment arm for Y component | ft | 7.5 | 7.5 |  |  | 11 | 11 | [9 empty] | Overturn moment arm for Y component | ft | 7.5 | 7.5 |  |  | 11 | 11
| Overturn moment arm for Z component | ft | 40 | 0 |  |  | 40 | 0 | 37.25 | 31.75 | 23.5 | 9 | 37.25 | 31.75 | 23.5 | 9 |  | Overturn moment arm for Z component | ft | 40 | 0 |  |  | 40 | 0 | 37.25 | 31.75 | 23.5 | 9 | 37.25 | 31.75 | 23.5 | 9 |  | Overturn moment arm for Z component | ft | 40 | 0 |  |  | 40 | 0 | 37.25 | 31.75 | 23.5 | 9 | 37.25 | 31.75 | 23.5 | 9 |  | Overturn moment arm for Z component | ft | 40 | 0 |  |  | 40 | 0 | 37.25 | 31.75 | 23.5 | 9 | 37.25 | 31.75 | 23.5 | 9 |  | Overturn moment arm for Z component | ft | 20 | 0 |  |  | 15 | 5 | [9 empty] | Overturn moment arm for Z component | ft | 20 | 0 |  |  | 15 | 5 | [9 empty] | Overturn moment arm for Z component | ft | 20 | 0 |  |  | 15 | 5 | [9 empty] | Overturn moment arm for Z component | ft | 20 | 0 |  |  | 15 | 5
| Pressure for OPEN using Part.-encl. value for gable wall | lbs/ft2 | 0.13714 | -0.84924 |  |  | 0.13714 | -0.84924 | -0.71737 | -0.71737 | -0.53803 | -0.26901 | -0.71737 | -0.71737 | -0.53803 | -0.26901 |  | Pressure for OPEN using Part.-encl. value for gable wall | lbs/ft2 | 0.13714 | -0.84924 |  |  | 0.13714 | -0.84924 | 0.71737 | 0.71737 | 0.44836 | 0.26901 | 0.71737 | 0.71737 | 0.44836 | 0.26901 |  | Pressure for OPEN using Part.-encl. value for gable wall | lbs/ft2 | 1.2976 | 0.31121 |  |  | 1.2976 | 0.31121 | -1.0761 | -1.0761 | -0.80704 | -0.53803 | -1.0761 | -1.0761 | -0.80704 | -0.53803 |  | Pressure for OPEN using Part.-encl. value for gable wall | lbs/ft2 | 1.2976 | 0.31121 |  |  | 1.2976 | 0.31121 | 0.44836 | 0.44836 | 0.44836 | 0.26901 | 0.44836 | 0.44836 | 0.44836 | 0.26901 |  | Pressure for OPEN using Part.-encl. value for gable wall | lbs/ft2 | 0.13714 | -1.0286 |  |  | 0.13714 | -1.0286 | [9 empty] | Pressure for OPEN using Part.-encl. value for gable wall | lbs/ft2 | 0.13714 | -1.0286 |  |  | 0.13714 | -1.0286 | [9 empty] | Pressure for OPEN using Part.-encl. value for gable wall | lbs/ft2 | 1.2976 | 0.13187 |  |  | 1.2976 | 0.13187 | [9 empty] | Pressure for OPEN using Part.-encl. value for gable wall | lbs/ft2 | 1.2976 | 0.13187 |  |  | 1.2976 | 0.13187
| Horizontal force (+ in X) | lbs | -2.7429 | -16.9848 |  |  | -8.2286 | -50.9543 | [9 empty] | Horizontal force (+ in X) | lbs | -2.7429 | -16.9848 |  |  | -8.2286 | -50.9543 | [9 empty] | Horizontal force (+ in X) | lbs | -25.9519 | 6.2242 |  |  | -77.8557 | 18.6727 | [9 empty] | Horizontal force (+ in X) | lbs | -25.9519 | 6.2242 |  |  | -77.8557 | 18.6727 | [9 empty] | Horizontal force (+ in X) | lbs | [15 empty] | Horizontal force (+ in X) | lbs | [15 empty] | Horizontal force (+ in X) | lbs | [15 empty] | Horizontal force (+ in X) | lbs
| Horizontal force (+ in Y) | lbs | [6 empty] | 23.6732 | 23.6732 | 35.5098 | 29.0535 | -23.6732 | -23.6732 | -35.5098 | -29.0535 |  | Horizontal force (+ in Y) | lbs | [6 empty] | -23.6732 | -23.6732 | -29.5915 | -29.0535 | 23.6732 | 23.6732 | 29.5915 | 29.0535 |  | Horizontal force (+ in Y) | lbs | [6 empty] | 35.5098 | 35.5098 | 53.2647 | 58.1069 | -35.5098 | -35.5098 | -53.2647 | -58.1069 |  | Horizontal force (+ in Y) | lbs | [6 empty] | -14.7957 | -14.7957 | -29.5915 | -29.0535 | 14.7957 | 14.7957 | 29.5915 | 29.0535 |  | Horizontal force (+ in Y) | lbs | -5.4858 | -41.1432 |  |  | -16.4573 | -123.4297 | [9 empty] | Horizontal force (+ in Y) | lbs | -5.4858 | -41.1432 |  |  | -16.4573 | -123.4297 | [9 empty] | Horizontal force (+ in Y) | lbs | -51.9038 | 5.2748 |  |  | -155.7114 | 15.8243 | [9 empty] | Horizontal force (+ in Y) | lbs | -51.9038 | 5.2748 |  |  | -155.7114 | 15.8243
| Vertical force (+ in Z) | lbs | [6 empty] | 39.4553 | 39.4553 | 59.183 | 48.4224 | 39.4553 | 39.4553 | 59.183 | 48.4224 |  | Vertical force (+ in Z) | lbs | [6 empty] | -39.4553 | -39.4553 | -49.3191 | -48.4224 | -39.4553 | -39.4553 | -49.3191 | -48.4224 |  | Vertical force (+ in Z) | lbs | [6 empty] | 59.183 | 59.183 | 88.7745 | 96.8449 | 59.183 | 59.183 | 88.7745 | 96.8449 |  | Vertical force (+ in Z) | lbs | [6 empty] | -24.6596 | -24.6596 | -49.3191 | -48.4224 | -24.6596 | -24.6596 | -49.3191 | -48.4224 |  | Vertical force (+ in Z) | lbs |  |  |  |  | -27.4288 | 205.7162 | [9 empty] | Vertical force (+ in Z) | lbs |  |  |  |  | -27.4288 | 205.7162 | [9 empty] | Vertical force (+ in Z) | lbs |  |  |  |  | -259.5189 | -26.3739 | [9 empty] | Vertical force (+ in Z) | lbs |  |  |  |  | -259.5189 | -26.3739
| Overturn moment | lbs.ft | -20.5716 | -127.3858 |  |  | -82.2865 | -509.5433 | -1469.7107 | -1252.7064 | -1390.8 | -435.8019 | -1469.7107 | -1252.7064 | -1390.8 | -435.8019 |  | Overturn moment | lbs.ft | -20.5716 | -127.3858 |  |  | -82.2865 | -509.5433 | 1469.7107 | 1252.7064 | 1159 | 435.8019 | 1469.7107 | 1252.7064 | 1159 | 435.8019 |  | Overturn moment | lbs.ft | -194.6392 | 46.6818 |  |  | -778.5568 | 186.727 | -2204.566 | -1879.0596 | -2086.2 | -871.6039 | -2204.566 | -1879.0596 | -2086.2 | -871.6039 |  | Overturn moment | lbs.ft | -194.6392 | 46.6818 |  |  | -778.5568 | 186.727 | 918.5692 | 782.9415 | 1159 | 435.8019 | 918.5692 | 782.9415 | 1159 | 435.8019 |  | Overturn moment | lbs.ft | -41.1432 | -308.5744 |  |  | -592.4628 | -329.146 | [9 empty] | Overturn moment | lbs.ft | -41.1432 | -308.5744 |  |  | -592.4628 | -329.146 | [9 empty] | Overturn moment | lbs.ft | -389.2784 | 39.5608 |  |  | -5605.6093 | 42.1982 | [9 empty] | Overturn moment | lbs.ft | -389.2784 | 39.5608 |  |  | -5605.6093 | 42.1982
| Total horizontal force (+ in X) | lbs | -78.9106 | [14 empty] | Total horizontal force (+ in X) | lbs | -78.9106 | [14 empty] | Total horizontal force (+ in X) | lbs | -78.9106 | [14 empty] | Total horizontal force (+ in X) | lbs | -78.9106 | [14 empty] | Total horizontal force (+ in X) | lbs | 0 | [14 empty] | Total horizontal force (+ in X) | lbs | 0 | [14 empty] | Total horizontal force (+ in X) | lbs | 0 | [14 empty] | Total horizontal force (+ in X) | lbs | 0
| Total horizontal force (+ in Y) | lbs | 2.8422e-14 | [14 empty] | Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | -186.5161 | [14 empty] | Total horizontal force (+ in Y) | lbs | -186.5161 | [14 empty] | Total horizontal force (+ in Y) | lbs | -186.5161 | [14 empty] | Total horizontal force (+ in Y) | lbs | -186.5161
| Total vertical force (+ in Z) | lbs | 373.0321 | [14 empty] | Total vertical force (+ in Z) | lbs | -353.3045 | [14 empty] | Total vertical force (+ in Z) | lbs | 607.9706 | [14 empty] | Total vertical force (+ in Z) | lbs | -294.1215 | [14 empty] | Total vertical force (+ in Z) | lbs | 178.2874 | [14 empty] | Total vertical force (+ in Z) | lbs | 178.2874 | [14 empty] | Total vertical force (+ in Z) | lbs | -285.8928 | [14 empty] | Total vertical force (+ in Z) | lbs | -285.8928
| Overturn moment | lbs.ft | -9837.8253 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 7894.6508 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -14822.6463 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 5852.838 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -1271.3264 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -1271.3264 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -5913.1287 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -5913.1287 | Must be POSITIVE for overturn
9.2 - FORCES FOR PARTIALLY ENCLOSED | [16 empty] | 9.2 - FORCES FOR PARTIALLY ENCLOSED | [16 empty] | 9.2 - FORCES FOR PARTIALLY ENCLOSED | [16 empty] | 9.2 - FORCES FOR PARTIALLY ENCLOSED | [16 empty] | 9.2 - FORCES FOR PARTIALLY ENCLOSED | [16 empty] | 9.2 - FORCES FOR PARTIALLY ENCLOSED | [16 empty] | 9.2 - FORCES FOR PARTIALLY ENCLOSED | [16 empty] | 9.2 - FORCES FOR PARTIALLY ENCLOSED
Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface | [16 empty] | Step 9: Calculate total force applied on each building surface
| Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +X | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y | [15 empty] | Winward wall | +Y
| Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -X | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y | [15 empty] | Leeward wall | -Y
| Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +Y | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X | [15 empty] | Side Wall 1 | +X
| Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -Y | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X | [15 empty] | Side Wall 2 | -X
| Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +X | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y | [15 empty] | Winward roof | +Y
| Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -X | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y | [15 empty] | Leeward roof | -Y
| Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +Y | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X | [15 empty] | Roof side 1 | +X
| Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -Y | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X | [15 empty] | Roof side 2 | -X
| Dimension parallel to wind direction | 40 | [15 empty] | Dimension parallel to wind direction | 40 | [15 empty] | Dimension parallel to wind direction | 40 | [15 empty] | Dimension parallel to wind direction | 40 | [15 empty] | Dimension parallel to wind direction | 20 | [15 empty] | Dimension parallel to wind direction | 20 | [15 empty] | Dimension parallel to wind direction | 20 | [15 empty] | Dimension parallel to wind direction | 20
| Dimension perpendicular to wind direction | 20 | [15 empty] | Dimension perpendicular to wind direction | 20 | [15 empty] | Dimension perpendicular to wind direction | 20 | [15 empty] | Dimension perpendicular to wind direction | 20 | [15 empty] | Dimension perpendicular to wind direction | 40 | [15 empty] | Dimension perpendicular to wind direction | 40 | [15 empty] | Dimension perpendicular to wind direction | 40 | [15 empty] | Dimension perpendicular to wind direction | 40
| Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0 | [15 empty] | Ridge length parallel to wind direction | 0
| Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0 | [15 empty] | Ridge length perpendicular to wind direction | 0
| Pitch angle of roof parallel to wind direction | 30.9638 | [15 empty] | Pitch angle of roof parallel to wind direction | 30.9638 | [15 empty] | Pitch angle of roof parallel to wind direction | 30.9638 | [15 empty] | Pitch angle of roof parallel to wind direction | 30.9638 | [15 empty] | Pitch angle of roof parallel to wind direction | 16.6993 | [15 empty] | Pitch angle of roof parallel to wind direction | 16.6993 | [15 empty] | Pitch angle of roof parallel to wind direction | 16.6993 | [15 empty] | Pitch angle of roof parallel to wind direction | 16.6993
| Pitch angle of roof perpendicular to wind direction | 16.6993 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 16.6993 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 16.6993 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 16.6993 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 30.9638 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 30.9638 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 30.9638 | [15 empty] | Pitch angle of roof perpendicular to wind direction | 30.9638
| Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8 | [15 empty] | Eave height | 8
| Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11 | [15 empty] | Mean roof height | 11
| Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6 | [15 empty] | Roof height | 6
| PARTIALLY ENCLOSED | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | PARTIALLY ENCLOSED | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | PARTIALLY ENCLOSED | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | PARTIALLY ENCLOSED | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | PARTIALLY ENCLOSED | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | PARTIALLY ENCLOSED | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | PARTIALLY ENCLOSED | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge |  |  |  |  | PARTIALLY ENCLOSED | [7 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge
[9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h
|  |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 | [6 empty] | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2
|  |  | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X
| X-component of normal vector (+inward) |  | -1 | 1 | 0 | 0 | -0.28735 | 0.28735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | -1 | 1 | 0 | 0 | -0.28735 | 0.28735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | -1 | 1 | 0 | 0 | -0.28735 | 0.28735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | -1 | 1 | 0 | 0 | -0.28735 | 0.28735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | X-component of normal vector (+inward) |  | 0 | 0 | -1 | 1 | 0 | 0 | -0.28735 | -0.28735 | -0.28735 | -0.28735 | 0.28735 | 0.28735 | 0.28735 | 0.28735 |  | X-component of normal vector (+inward) |  | 0 | 0 | -1 | 1 | 0 | 0 | -0.28735 | -0.28735 | -0.28735 | -0.28735 | 0.28735 | 0.28735 | 0.28735 | 0.28735 |  | X-component of normal vector (+inward) |  | 0 | 0 | -1 | 1 | 0 | 0 | -0.28735 | -0.28735 | -0.28735 | -0.28735 | 0.28735 | 0.28735 | 0.28735 | 0.28735 |  | X-component of normal vector (+inward) |  | 0 | 0 | -1 | 1 | 0 | 0 | -0.28735 | -0.28735 | -0.28735 | -0.28735 | 0.28735 | 0.28735 | 0.28735 | 0.28735
| Y-component of normal vector (+inward) |  | 0 | 0 | -1 | 1 | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | 0 | 0 | -1 | 1 | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | 0 | 0 | -1 | 1 | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | 0 | 0 | -1 | 1 | 0 | 0 | -0.5145 | -0.5145 | -0.5145 | -0.5145 | 0.5145 | 0.5145 | 0.5145 | 0.5145 |  | Y-component of normal vector (+inward) |  | -1 | 1 | 0 | 0 | -0.5145 | 0.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Y-component of normal vector (+inward) |  | -1 | 1 | 0 | 0 | -0.5145 | 0.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Y-component of normal vector (+inward) |  | -1 | 1 | 0 | 0 | -0.5145 | 0.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Y-component of normal vector (+inward) |  | -1 | 1 | 0 | 0 | -0.5145 | 0.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Z-component of normal vector (+inward) |  | 0 | 0 | 0 | 0 | -0.95783 | -0.95783 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 | 0 | 0 | -0.95783 | -0.95783 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 | 0 | 0 | -0.95783 | -0.95783 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 | 0 | 0 | -0.95783 | -0.95783 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 | -0.85749 |  | Z-component of normal vector (+inward) |  | 0 | 0 | 0 | 0 | -0.85749 | -0.85749 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 |  | Z-component of normal vector (+inward) |  | 0 | 0 | 0 | 0 | -0.85749 | -0.85749 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 |  | Z-component of normal vector (+inward) |  | 0 | 0 | 0 | 0 | -0.85749 | -0.85749 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 |  | Z-component of normal vector (+inward) |  | 0 | 0 | 0 | 0 | -0.85749 | -0.85749 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783 | -0.95783
| Overturn moment arm for X component | ft | 4 | 4 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 4 | 4 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 4 | 4 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 4 | 4 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for X component | ft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Overturn moment arm for Y component | ft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 4 | 4 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 4 | 4 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 4 | 4 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Overturn moment arm for Y component | ft | 4 | 4 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Overturn moment arm for Z component | ft | 0 | 0 | 0 | 0 | 33.3333 | 6.6667 | 36.3333 | 31.4444 | 22.984 | 12 | 36.3333 | 31.4444 | 22.984 | 12 |  | Overturn moment arm for Z component | ft | 0 | 0 | 0 | 0 | 33.3333 | 6.6667 | 36.3333 | 31.4444 | 22.984 | 12 | 36.3333 | 31.4444 | 22.984 | 12 |  | Overturn moment arm for Z component | ft | 0 | 0 | 0 | 0 | 33.3333 | 6.6667 | 36.3333 | 31.4444 | 22.984 | 12 | 36.3333 | 31.4444 | 22.984 | 12 |  | Overturn moment arm for Z component | ft | 0 | 0 | 0 | 0 | 33.3333 | 6.6667 | 36.3333 | 31.4444 | 22.984 | 12 | 36.3333 | 31.4444 | 22.984 | 12 |  | Overturn moment arm for Z component | ft | 0 | 0 | 0 | 0 | 16.6667 | 3.3333 | 16.3333 | 11.492 | 6 | 20 | 16.3333 | 11.492 | 6 | 20 |  | Overturn moment arm for Z component | ft | 0 | 0 | 0 | 0 | 16.6667 | 3.3333 | 16.3333 | 11.492 | 6 | 20 | 16.3333 | 11.492 | 6 | 20 |  | Overturn moment arm for Z component | ft | 0 | 0 | 0 | 0 | 16.6667 | 3.3333 | 16.3333 | 11.492 | 6 | 20 | 16.3333 | 11.492 | 6 | 20 |  | Overturn moment arm for Z component | ft | 0 | 0 | 0 | 0 | 16.6667 | 3.3333 | 16.3333 | 11.492 | 6 | 20 | 16.3333 | 11.492 | 6 | 20
| Horizontal force (+ in X) | lbs | -21.9431 | -135.8782 | 0 | 0 | 58.9511 | -63.5434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in X) | lbs | -21.9431 | -135.8782 | 0 | 0 | 32.1615 | -63.5434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in X) | lbs | -207.6152 | 49.7939 | 0 | 0 | -10.6759 | 6.0837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in X) | lbs | -207.6152 | 49.7939 | 0 | 0 | -37.4655 | 6.0837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in X) | lbs | 0 | 0 | 193.2678 | -193.2678 | 0 | 0 | 12.9149 | 36.4585 | 25.4303 | 0 | -12.9149 | -36.4585 | -25.4303 | 0 |  | Horizontal force (+ in X) | lbs | 0 | 0 | 193.2678 | -193.2678 | 0 | 0 | 6.7303 | 19.746 | 18.0217 | 0 | -6.7303 | -19.746 | -18.0217 | 0 |  | Horizontal force (+ in X) | lbs | 0 | 0 | 7.5957 | -7.5957 | 0 | 0 | 2.3839 | 5.5615 | -2.7686 | 0 | -2.3839 | -5.5615 | 2.7686 | 0 |  | Horizontal force (+ in X) | lbs | 0 | 0 | 7.5957 | -7.5957 | 0 | 0 | -3.8008 | -11.151 | -10.1773 | 0 | 3.8008 | 11.151 | 10.1773 | 0
| Horizontal force (+ in Y) | lbs | 0 | 0 | 386.5355 | -386.5355 | 0 | 0 | 6.2947 | 18.8842 | 54.7719 | 41.273 | -6.2947 | -18.8842 | -54.7719 | -41.273 |  | Horizontal force (+ in Y) | lbs | 0 | 0 | 386.5355 | -386.5355 | 0 | 0 | 3.3652 | 10.0955 | 39.492 | 36.0434 | -3.3652 | -10.0955 | -39.492 | -36.0434 |  | Horizontal force (+ in Y) | lbs | 0 | 0 | 15.1914 | -15.1914 | 0 | 0 | 1.0292 | 3.0875 | -7.022 | -15.1249 | -1.0292 | -3.0875 | 7.022 | 15.1249 |  | Horizontal force (+ in Y) | lbs | 0 | 0 | 15.1914 | -15.1914 | 0 | 0 | -1.9004 | -5.7011 | -22.302 | -20.3545 | 1.9004 | 5.7011 | 22.302 | 20.3545 |  | Horizontal force (+ in Y) | lbs | -43.8861 | -329.146 | 0 | 0 | 92.0168 | -134.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in Y) | lbs | -43.8861 | -329.146 | 0 | 0 | 46.2392 | -134.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in Y) | lbs | -415.2303 | 42.1982 | 0 | 0 | -47.2373 | 5.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Horizontal force (+ in Y) | lbs | -415.2303 | 42.1982 | 0 | 0 | -93.0149 | 5.0638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | 196.5036 | 211.8112 | 10.4912 | 31.4736 | 91.2866 | 68.7883 | 10.4912 | 31.4736 | 91.2866 | 68.7883 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | 107.2052 | 211.8112 | 5.6086 | 16.8258 | 65.82 | 60.0723 | 5.6086 | 16.8258 | 65.82 | 60.0723 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | -35.5865 | -20.2789 | 1.7153 | 5.1459 | -11.7034 | -25.2082 | 1.7153 | 5.1459 | -11.7034 | -25.2082 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | -124.885 | -20.2789 | -3.1673 | -9.5019 | -37.17 | -33.9242 | -3.1673 | -9.5019 | -37.17 | -33.9242 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | 153.3613 | 223.6505 | 43.0498 | 121.5282 | 84.7678 | 0 | 43.0498 | 121.5282 | 84.7678 | 0 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | 77.0653 | 223.6505 | 22.4344 | 65.82 | 60.0723 | 0 | 22.4344 | 65.82 | 60.0723 | 0 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | -78.7289 | -8.4396 | 7.9462 | 18.5382 | -9.2287 | 0 | 7.9462 | 18.5382 | -9.2287 | 0 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | -155.0248 | -8.4396 | -12.6692 | -37.17 | -33.9242 | 0 | -12.6692 | -37.17 | -33.9242 | 0
| Overturn moment | lbs.ft | -87.7723 | -543.5129 | 0 | 0 | -5960.6101 | -2047.5085 | -381.1802 | -989.6697 | -2098.1342 | -825.4601 | -381.1802 | -989.6697 | -2098.1342 | -825.4601 |  | Overturn moment | lbs.ft | -87.7723 | -543.5129 | 0 | 0 | -3251.8899 | -2047.5085 | -203.7792 | -529.0782 | -1512.8086 | -720.8677 | -203.7792 | -529.0782 | -1512.8086 | -720.8677 |  | Overturn moment | lbs.ft | -830.4606 | 199.1755 | 0 | 0 | 1079.4568 | 196.0293 | -62.3222 | -161.8091 | 268.9916 | 302.4978 | -62.3222 | -161.8091 | 268.9916 | 302.4978 |  | Overturn moment | lbs.ft | -830.4606 | 199.1755 | 0 | 0 | 3788.177 | 196.0293 | 115.0787 | 298.7824 | 854.3172 | 407.0903 | 115.0787 | 298.7824 | 854.3172 | 407.0903 |  | Overturn moment | lbs.ft | 175.5445 | 1316.5839 | 0 | 0 | 1635.8534 | 2087.4044 | 703.147 | 1396.6042 | 508.6065 | 0 | 703.147 | 1396.6042 | 508.6065 | 0 |  | Overturn moment | lbs.ft | 175.5445 | 1316.5839 | 0 | 0 | 822.0303 | 2087.4044 | 366.4287 | 756.4043 | 360.4338 | 0 | 366.4287 | 756.4043 | 360.4338 | 0 |  | Overturn moment | lbs.ft | 1660.9213 | -168.7928 | 0 | 0 | -839.7745 | -78.77 | 129.7877 | 213.0413 | -55.3725 | 0 | 129.7877 | 213.0413 | -55.3725 | 0 |  | Overturn moment | lbs.ft | 1660.9213 | -168.7928 | 0 | 0 | -1653.5976 | -78.77 | -206.9306 | -427.1586 | -203.5451 | 0 | -206.9306 | -427.1586 | -203.5451 | 0
| Total horizontal force (+ in X) | lbs | -162.4136 | [14 empty] | Total horizontal force (+ in X) | lbs | -189.2031 | [14 empty] | Total horizontal force (+ in X) | lbs | -162.4136 | [14 empty] | Total horizontal force (+ in X) | lbs | -189.2031 | [14 empty] | Total horizontal force (+ in X) | lbs | 3.5527e-15 | [14 empty] | Total horizontal force (+ in X) | lbs | 0 | [14 empty] | Total horizontal force (+ in X) | lbs | 0 | [14 empty] | Total horizontal force (+ in X) | lbs | 0
| Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | -415.2056 | [14 empty] | Total horizontal force (+ in Y) | lbs | -460.9832 | [14 empty] | Total horizontal force (+ in Y) | lbs | -415.2056 | [14 empty] | Total horizontal force (+ in Y) | lbs | -460.9832
| Total vertical force (+ in Z) | lbs | 812.3943 | [14 empty] | Total vertical force (+ in Z) | lbs | 615.6697 | [14 empty] | Total vertical force (+ in Z) | lbs | -115.9662 | [14 empty] | Total vertical force (+ in Z) | lbs | -312.6907 | [14 empty] | Total vertical force (+ in Z) | lbs | 875.7032 | [14 empty] | Total vertical force (+ in Z) | lbs | 597.3692 | [14 empty] | Total vertical force (+ in Z) | lbs | -52.6572 | [14 empty] | Total vertical force (+ in Z) | lbs | -330.9913
| Overturn moment | lbs.ft | -17228.2922 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -11863.7508 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 1338.9171 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 6703.4585 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 10432.1017 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 7368.0968 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 1148.4971 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -1915.5078 | Must be POSITIVE for overturn
[9 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge | [12 empty] | Horizontal distance from windward edge |  |  |  | Horizontal distance from windward edge
[9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h | [9 empty] | 0-h/2 | h/2-h | h-2h | >2h | 0-h/2 | h/2-h | h-2h | >2h
| IF GABLE ROOF |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2 |  |  |  |  | IF GABLE ROOF |  | WinWall | LeeWall | SideWall1 | SideWall2 | WinRoof | LeeRoof | Roof Side 1 |  |  |  | Roof Side 2
|  |  | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +X | -X | +Y | -Y | +X | -X | +Y |  |  |  | -Y | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X | [6 empty] | +Y | -Y | +X | -X | +Y | -Y | +X |  |  |  | -X
| Areas | ft2 |  |  |  |  | 60 | 60 | 64.1405 | 64.1405 | 128.2809 | 209.9143 | [5 empty] | Areas | ft2 |  |  |  |  | 60 | 60 | 64.1405 | 64.1405 | 128.2809 | 209.9143 | [5 empty] | Areas | ft2 |  |  |  |  | 60 | 60 | 64.1405 | 64.1405 | 128.2809 | 209.9143 | [5 empty] | Areas | ft2 |  |  |  |  | 60 | 60 | 64.1405 | 64.1405 | 128.2809 | 209.9143 | [5 empty] | Areas | ft2 |  |  |  |  | 233.2381 | 233.2381 | [9 empty] | Areas | ft2 |  |  |  |  | 233.2381 | 233.2381 | [9 empty] | Areas | ft2 |  |  |  |  | 233.2381 | 233.2381 | [9 empty] | Areas | ft2 |  |  |  |  | 233.2381 | 233.2381
| X-component of normal vector (+inward) | [5 empty] | -1 | 1 | 0 | 0 | 0 | 0 | [5 empty] | X-component of normal vector (+inward) | [5 empty] | -1 | 1 | 0 | 0 | 0 | 0 | [5 empty] | X-component of normal vector (+inward) | [5 empty] | -1 | 1 | 0 | 0 | 0 | 0 | [5 empty] | X-component of normal vector (+inward) | [5 empty] | -1 | 1 | 0 | 0 | 0 | 0 | [5 empty] | X-component of normal vector (+inward) | [5 empty] | 0 | 0 | [9 empty] | X-component of normal vector (+inward) | [5 empty] | 0 | 0 | [9 empty] | X-component of normal vector (+inward) | [5 empty] | 0 | 0 | [9 empty] | X-component of normal vector (+inward) | [5 empty] | 0 | 0
| Y-component of normal vector (+inward) | [7 empty] | -0.5145 | -0.5145 | -0.5145 | -0.5145 | [5 empty] | Y-component of normal vector (+inward) | [7 empty] | -0.5145 | -0.5145 | -0.5145 | -0.5145 | [5 empty] | Y-component of normal vector (+inward) | [7 empty] | -0.5145 | -0.5145 | -0.5145 | -0.5145 | [5 empty] | Y-component of normal vector (+inward) | [7 empty] | -0.5145 | -0.5145 | -0.5145 | -0.5145 | [5 empty] | Y-component of normal vector (+inward) | [5 empty] | -0.5145 | 0.5145 | [9 empty] | Y-component of normal vector (+inward) | [5 empty] | -0.5145 | 0.5145 | [9 empty] | Y-component of normal vector (+inward) | [5 empty] | -0.5145 | 0.5145 | [9 empty] | Y-component of normal vector (+inward) | [5 empty] | -0.5145 | 0.5145
| Z-component of normal vector (+inward) | [7 empty] | -0.85749 | -0.85749 | -0.85749 | -0.85749 | [5 empty] | Z-component of normal vector (+inward) | [7 empty] | -0.85749 | -0.85749 | -0.85749 | -0.85749 | [5 empty] | Z-component of normal vector (+inward) | [7 empty] | -0.85749 | -0.85749 | -0.85749 | -0.85749 | [5 empty] | Z-component of normal vector (+inward) | [7 empty] | -0.85749 | -0.85749 | -0.85749 | -0.85749 | [5 empty] | Z-component of normal vector (+inward) | [5 empty] | -0.85749 | -0.85749 | [9 empty] | Z-component of normal vector (+inward) | [5 empty] | -0.85749 | -0.85749 | [9 empty] | Z-component of normal vector (+inward) | [5 empty] | -0.85749 | -0.85749 | [9 empty] | Z-component of normal vector (+inward) | [5 empty] | -0.85749 | -0.85749
| Overturn moment arm for X component | ft |  |  |  |  | 10 | 10 | 0 | 0 | 0 | 0 | [5 empty] | Overturn moment arm for X component | ft |  |  |  |  | 10 | 10 | 0 | 0 | 0 | 0 | [5 empty] | Overturn moment arm for X component | ft |  |  |  |  | 10 | 10 | 0 | 0 | 0 | 0 | [5 empty] | Overturn moment arm for X component | ft |  |  |  |  | 10 | 10 | 0 | 0 | 0 | 0 | [5 empty] | Overturn moment arm for X component | ft |  |  |  |  | 0 | 10 | [9 empty] | Overturn moment arm for X component | ft |  |  |  |  | 0 | 10 | [9 empty] | Overturn moment arm for X component | ft |  |  |  |  | 0 | 10 | [9 empty] | Overturn moment arm for X component | ft |  |  |  |  | 0 | 10
| Overturn moment arm for Y component | ft | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | Overturn moment arm for Y component | ft | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | Overturn moment arm for Y component | ft | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | Overturn moment arm for Y component | ft | [6 empty] | 0 | 0 | 0 | 0 | [5 empty] | Overturn moment arm for Y component | ft |  |  |  |  | 11 | 11 | [9 empty] | Overturn moment arm for Y component | ft |  |  |  |  | 11 | 11 | [9 empty] | Overturn moment arm for Y component | ft |  |  |  |  | 11 | 11 | [9 empty] | Overturn moment arm for Y component | ft |  |  |  |  | 11 | 11
| Overturn moment arm for Z component | ft | [6 empty] | 37.25 | 31.75 | 23.5 | 9 | [5 empty] | Overturn moment arm for Z component | ft | [6 empty] | 37.25 | 31.75 | 23.5 | 9 | [5 empty] | Overturn moment arm for Z component | ft | [6 empty] | 37.25 | 31.75 | 23.5 | 9 | [5 empty] | Overturn moment arm for Z component | ft | [6 empty] | 37.25 | 31.75 | 23.5 | 9 | [5 empty] | Overturn moment arm for Z component | ft |  |  |  |  | 15 | 5 | [9 empty] | Overturn moment arm for Z component | ft |  |  |  |  | 15 | 5 | [9 empty] | Overturn moment arm for Z component | ft |  |  |  |  | 15 | 5 | [9 empty] | Overturn moment arm for Z component | ft |  |  |  |  | 15 | 5
| Pressure for PARTIALLY-ENCLOSED | lbs/ft2 | 0.13714 | -0.84924 | -1.2079 | -1.2079 | 0.13714 | -0.84924 | -1.3873 | -1.3873 | -1.0286 | -0.84924 | [5 empty] | Pressure for PARTIALLY-ENCLOSED | lbs/ft2 | 0.13714 | -0.84924 | -1.2079 | -1.2079 | 0.13714 | -0.84924 | -0.74163 | -0.74163 | -0.74163 | -0.74163 | [5 empty] | Pressure for PARTIALLY-ENCLOSED | lbs/ft2 | 1.2976 | 0.31121 | -0.047473 | -0.047473 | 1.2976 | 0.31121 | -0.22682 | -0.22682 | 0.13187 | 0.31121 | [5 empty] | Pressure for PARTIALLY-ENCLOSED | lbs/ft2 | 1.2976 | 0.31121 | -0.047473 | -0.047473 | 1.2976 | 0.31121 | 0.41882 | 0.41882 | 0.41882 | 0.41882 | [5 empty] | Pressure for PARTIALLY-ENCLOSED | lbs/ft2 | 0.13714 | -1.0286 | -1.2079 | -1.2079 | 0.13714 | -1.0286 | [9 empty] | Pressure for PARTIALLY-ENCLOSED | lbs/ft2 | 0.13714 | -1.0286 | -1.2079 | -1.2079 | 0.13714 | -1.0286 | [9 empty] | Pressure for PARTIALLY-ENCLOSED | lbs/ft2 | 1.2976 | 0.13187 | -0.047473 | -0.047473 | 1.2976 | 0.13187 | [9 empty] | Pressure for PARTIALLY-ENCLOSED | lbs/ft2 | 1.2976 | 0.13187 | -0.047473 | -0.047473 | 1.2976 | 0.13187
| Horizontal force (+ in X) | lbs | -21.9431 | -135.8782 | 0 | 0 | -8.2286 | -50.9543 | 0 | 0 | 0 | 0 | [5 empty] | Horizontal force (+ in X) | lbs | -21.9431 | -135.8782 | 0 | 0 | -8.2286 | -50.9543 | 0 | 0 | 0 | 0 | [5 empty] | Horizontal force (+ in X) | lbs | -207.6152 | 49.7939 | 0 | 0 | -77.8557 | 18.6727 | 0 | 0 | 0 | 0 | [5 empty] | Horizontal force (+ in X) | lbs | -207.6152 | 49.7939 | 0 | 0 | -77.8557 | 18.6727 | 0 | 0 | 0 | 0 | [5 empty] | Horizontal force (+ in X) | lbs | 0 | 0 | 193.2678 | -193.2678 | 0 | 0 | [9 empty] | Horizontal force (+ in X) | lbs | 0 | 0 | 193.2678 | -193.2678 | 0 | 0 | [9 empty] | Horizontal force (+ in X) | lbs | 0 | 0 | 7.5957 | -7.5957 | 0 | 0 | [9 empty] | Horizontal force (+ in X) | lbs | 0 | 0 | 7.5957 | -7.5957 | 0 | 0
| Horizontal force (+ in Y) | lbs | 0 | 0 | 386.5355 | -386.5355 |  |  | 45.7798 | 45.7798 | 67.8864 | 91.7178 | -45.7798 | -45.7798 | -67.8864 | -91.7178 |  | Horizontal force (+ in Y) | lbs | 0 | 0 | 386.5355 | -386.5355 |  |  | 24.4739 | 24.4739 | 48.9478 | 80.0964 | -24.4739 | -24.4739 | -48.9478 | -80.0964 |  | Horizontal force (+ in Y) | lbs | 0 | 0 | 15.1914 | -15.1914 |  |  | 7.4849 | 7.4849 | -8.7034 | -33.6109 | -7.4849 | -7.4849 | 8.7034 | 33.6109 |  | Horizontal force (+ in Y) | lbs | 0 | 0 | 15.1914 | -15.1914 |  |  | -13.821 | -13.821 | -27.6419 | -45.2323 | 13.821 | 13.821 | 27.6419 | 45.2323 |  | Horizontal force (+ in Y) | lbs | -43.8861 | -329.146 | 0 | 0 | -16.4573 | -123.4297 | [9 empty] | Horizontal force (+ in Y) | lbs | -43.8861 | -329.146 | 0 | 0 | -16.4573 | -123.4297 | [9 empty] | Horizontal force (+ in Y) | lbs | -415.2303 | 42.1982 | 0 | 0 | -155.7114 | 15.8243 | [9 empty] | Horizontal force (+ in Y) | lbs | -415.2303 | 42.1982 | 0 | 0 | -155.7114 | 15.8243
| Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 |  |  | 76.2996 | 76.2996 | 113.1439 | 152.863 | 76.2996 | 76.2996 | 113.1439 | 152.863 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 |  |  | 40.7898 | 40.7898 | 81.5797 | 133.494 | 40.7898 | 40.7898 | 81.5797 | 133.494 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 |  |  | 12.4748 | 12.4748 | -14.5056 | -56.0181 | 12.4748 | 12.4748 | -14.5056 | -56.0181 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 |  |  | -23.0349 | -23.0349 | -46.0699 | -75.3871 | -23.0349 | -23.0349 | -46.0699 | -75.3871 |  | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | -27.4288 | 205.7162 | [9 empty] | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | -27.4288 | 205.7162 | [9 empty] | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | -259.5189 | -26.3739 | [9 empty] | Vertical force (+ in Z) | lbs | 0 | 0 | 0 | 0 | -259.5189 | -26.3739
| Overturn moment | lbs.ft | -87.7723 | -543.5129 | 0 | 0 | -82.2865 | -509.5433 | -2842.1611 | -2422.5131 | -2658.8824 | -1375.7669 | -2842.1611 | -2422.5131 | -2658.8824 | -1375.7669 |  | Overturn moment | lbs.ft | -87.7723 | -543.5129 | 0 | 0 | -82.2865 | -509.5433 | -1519.4215 | -1295.0774 | -1917.1224 | -1201.4461 | -1519.4215 | -1295.0774 | -1917.1224 | -1201.4461 |  | Overturn moment | lbs.ft | -830.4606 | 199.1755 | 0 | 0 | -778.5568 | 186.727 | -464.6879 | -396.0763 | 340.8824 | 504.163 | -464.6879 | -396.0763 | 340.8824 | 504.163 |  | Overturn moment | lbs.ft | -830.4606 | 199.1755 | 0 | 0 | -778.5568 | 186.727 | 858.0517 | 731.3595 | 1082.6424 | 678.4838 | 858.0517 | 731.3595 | 1082.6424 | 678.4838 |  | Overturn moment | lbs.ft | 175.5445 | 1316.5839 | 0 | 0 | -592.4628 | -329.146 | [9 empty] | Overturn moment | lbs.ft | 175.5445 | 1316.5839 | 0 | 0 | -592.4628 | -329.146 | [9 empty] | Overturn moment | lbs.ft | 1660.9213 | -168.7928 | 0 | 0 | -5605.6093 | 42.1982 | [9 empty] | Overturn moment | lbs.ft | 1660.9213 | -168.7928 | 0 | 0 | -5605.6093 | 42.1982
| Total horizontal force (+ in X) | lbs | -217.0043 | [14 empty] | Total horizontal force (+ in X) | lbs | -217.0043 | [14 empty] | Total horizontal force (+ in X) | lbs | -217.0043 | [14 empty] | Total horizontal force (+ in X) | lbs | -217.0043 | [14 empty] | Total horizontal force (+ in X) | lbs | 0 | [14 empty] | Total horizontal force (+ in X) | lbs | 0 | [14 empty] | Total horizontal force (+ in X) | lbs | 0 | [14 empty] | Total horizontal force (+ in X) | lbs | 0
| Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | 0 | [14 empty] | Total horizontal force (+ in Y) | lbs | -512.9192 | [14 empty] | Total horizontal force (+ in Y) | lbs | -512.9192 | [14 empty] | Total horizontal force (+ in Y) | lbs | -512.9192 | [14 empty] | Total horizontal force (+ in Y) | lbs | -512.9192
| Total vertical force (+ in Z) | lbs | 837.2123 | [14 empty] | Total vertical force (+ in Z) | lbs | 593.3067 | [14 empty] | Total vertical force (+ in Z) | lbs | -91.1481 | [14 empty] | Total vertical force (+ in Z) | lbs | -335.0537 | [14 empty] | Total vertical force (+ in Z) | lbs | 178.2874 | [14 empty] | Total vertical force (+ in Z) | lbs | 178.2874 | [14 empty] | Total vertical force (+ in Z) | lbs | -285.8928 | [14 empty] | Total vertical force (+ in Z) | lbs | -285.8928
| Overturn moment | lbs.ft | -19821.7619 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -13089.2496 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -1254.5526 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 5477.9597 | Must be NEGATIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 570.5197 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | 570.5197 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -4071.2826 | Must be POSITIVE for overturn | [13 empty] | Overturn moment | lbs.ft | -4071.2826 | Must be POSITIVE for overturn
Method 2: Wind exposure
|  |  |  | Roof |  |  | Walls | Valance | OPEN |  |  | PART-E
|  |  |  | Gable | Hip | Pyramid |  |  | Gable | Hip | Pyramid | Gable | Hip | Pyramid
|  | Fx | lbs | -61.44 | -61.44 | -61.44 | -163.84 | -20.48 | -81.92 | -81.92 | -81.92 | -225.28 | -225.28 | -225.28
|  | Fy | lbs | -245.76 | -184.32 | -122.88 | -327.68 | -40.96 | -286.72 | -225.28 | -163.84 | -573.44 | -512 | -450.56
|  | Mx | lbs.ft | 2703.36 | 1966.08 | 1228.8 | 1310.72 | 307.2 | 3010.56 | 2273.28 | 1536 | 4014.08 | 3276.8 | 2539.52
|  | My | lbs.ft | -614.4 | -614.4 | -614.4 | -655.36 | -153.6 | -768 | -768 | -768 | -1269.76 | -1269.76 | -1269.76
|  |  |  | OPEN | PART-E
|  | Fx | lbs | -81.92 | -225.28
|  | Fy | lbs | -163.84 | -450.56
|  | Mx | lbs.ft | 1536 | 2539.52
|  | My | lbs.ft | -768 | -1269.76